|  |  |  |
| --- | --- | --- |
| **wsu-primary-horz-color-600-10-2017-small****Division of Finance and Business Operations** |  | **Procurement & Strategic Sourcing** **5700 Cass Avenue, suite 4200****Detroit, Michigan 48202****(313) 577-3734**  |

**January 10, 2025**

**Addendum #3 To**

**Request for Proposal**

**For UGL Career Services: Project 096-414946**

**Dated December 23, 2024**

**The Addendum must be acknowledged on your lump sum bid.**

**Question:**

We need to confirm the heat register along the window is being removed to determine the path for the wire mold

**Answer:**

Yes, Heat register will be removed.

**Question:**

In the testing lab room, we need to know how many circuits you want us to provide for each piece of furniture?

**Answer:**

Provide 1 circuit for a 3-table row and 2 circuits for 4-tables row. (There are 11 total rows, in which 3 of these are 4-tables)

A copy of this Addendum will be posted to the Purchasing web site at

[**http://go.wayne.edu/bids**](http://go.wayne.edu/bids).

All questions concerning this project must be emailed to: **Valerie Kreher**, Procurement & Strategic Sourcing. Email: **rfpteam2@wayne.edu**.

Bids are due **by electronic submission on** no later than 2:00 p.m., **January 14, 2025.** The link for bid submission will be posted with the bid details at [**http://go.wayne.edu/bids**](http://go.wayne.edu/bids) beginning **December 23, 2024**.

Thank you,

**Valerie Kreher**,

**Senior Buyer**