| Division of Finance and Business Operations |  | Purchasing Department 5700 Cass Avenue, suite 4200 Detroit, Michigan 48202 (313) 577-3734 FAX (313) 577-3747 |
| --- | --- | --- |

July 8, 2013

Addendum #5 To

Request for Proposal

For Chatsworth Fire Alarm Panel: Project 136-195280

Dated June 18, 2013

Points of Clarifications after the Pre-proposal Meeting June 27, 2013:

The Addendum must be acknowledged on your lump sum bid.

IMPORTANT – PLEASE NOTE:  Effective December 1, 2007, bid notices will be sent only to those Vendors registered to receive them via our Bid Opportunities Listserve service.  To register, to http://www.forms.purchasing.wayne.edu/Adv_bid/Adv_bid.html, and click on the “Join our Listserve” link at the top of the page.  Instructions are at the top of the page, and the Construction Listserv service is under “Construction Bid Opportunities”.

NOTE: You must have attended a pre-bid conference in order to be eligible to bid on a particular project.  Receipt of minutes or addenda without being at a pre-bid conference does not qualify your company to bid.

Question 1:

Drawing F-7 calls for 65 psi at top of stand pipe. Current code requires 100 psi.

Answer:

The 65 psi is a typo on drawing and the pump is already designed for 100 psi per code.

Question 2:

Spec calls for schedule 40 steel pipe, can we use schedule 10 on pipes 2 inch and larger.

Answer:

Provide a price per the base bid. Voluntary alternates are acceptable.

Question 3:

Fire pump spec calls for split case pump, to reduce space restraints if available can we use an in-line model pump.

Answer:

Documents are adjusted to be an in-line model pump. See attached sheet M-4 (issued) and clarification of note on sheet F-7, and specification section 213113 (attached) .

Question 4:

Is there a time for an additional walk-through for subs to see some enclosed areas?  Mainly the basement and attic areas.

Answer:

A third walk through has been scheduled for July 9, 2013 at 1:00 pm. Contractors must meet in the Main Lobby of Chatsworth Apartments, 630 Williams Mall, Detroit, MI  48202. Questions will not be answered during the third walk-through.

A copy of this Addendum will be posted to the Purchasing web site at

http://www.forms.purchasing.wayne.edu/Adv_bid/Adv_bid.html.

As a reminder, the bid due date has been extended to July 12, 2013, at 2:00 pm.  If you have any further questions, please do not hesitate to email them to me at ac2843@wayne.edu and copy rfpteam1@wayne.edu.

Thank you,

Kimberly Tomaszewski for

Loretta McClary,

Senior Buyer