| Division of Finance and Business Operations |  | Procurement & Strategic Sourcing 5700 Cass Avenue, suite 4200 Detroit, Michigan 48202 (313) 577-3734 FAX (313) 577-3747 |
| --- | --- | --- |

June 30, 2016

Addendum #2 To

Request for Proposal

For IBio RadioChemistry Facility: Project 211-277899

Dated June 16, 2016

Points of Clarifications during the Pre-proposal Meeting June 23, 2016:

The Addendum must be acknowledged on your lump sum bid.

IMPORTANT – PLEASE NOTE:  Effective December 1, 2007, bid notices will be sent only to those Vendors registered to receive them via our Bid Opportunities Listserve service.  To register, to http://www.forms.procurement.wayne.edu/Adv_bid/Adv_bid.html, and click on the “Join our Listserve” link at the top of the page.  Instructions are at the top of the page, and the Construction Listserv service is under “Construction Bid Opportunities”.

NOTE: You must have attended a pre-bid conference in order to be eligible to bid on a particular project.  Receipt of minutes or addenda without being at a pre-bid conference does not qualify your company to bid.

Question:

Location of GAM-01 are not listed on the drawings only listed on the schedule.

Answer:

Refer to sheet AP-01 room 0003, west wall.

Question:

FC-01 is shown on North, South and East elevation? (Drawing A5-81)

Answer:

The FC-01 is identified in the schedule.

Question:

Drawings AP-01: Provide radiation monitor w/ remote readout LACO: model 375-10, digital area monitor (0.1mR/hr 9999 mR/hr)- Full spectrum w /options. 4396-171, model 375 red strobe and model 272D digital remote for model 375.  Did not mention on the spec, and who will provide and install it?

Answer:

The specific model is indicated on the drawing and not required to be listed in the specification.  To be furnished and installed by contractor.

Question:

Section 134900- X Ray Protection listed the lead-lined for gypsum board and doors and frames, on drawings only mentioned on the gypsum board?

Answer:

Lead lining is not required in the door or door frames per the WSU physicist’s report. Drawings provide the scope of lead shielding.

Question:

Who is will provide and install the leaded shield panel and the shelf leaded bricks?

Answer:

Contractor or contractor’s sub-contractors.

Question:

There are no drawings for card reader, voice and data systems?

Answer:

Refer to sheet AP-01 and EQ-0Bf.

A copy of this Addendum will be posted to the Purchasing web site at

http://www.forms.procurement.wayne.edu/Adv_bid/Adv_bid.html.

As a reminder, the bid due date is July 8, 2016, at 2:00 pm.  If you have any further questions, please do not hesitate to email them to me at rfpteam2@wayne.edu and copy leiann.day@wayne.edu.

Thank you,

Valerie Kreher,

Senior Buyer