| Division of Finance and Business Operations |  | Procurement & Strategic Sourcing 5700 Cass Avenue, suite 4200 Detroit, Michigan 48202 (313) 577-3734 FAX (313) 577-3747 |
| --- | --- | --- |

June 26, 2017

Addendum #1 To

Request for Proposal

For the Physics  Building Fire Alarm Replacement: Project 003-240915

Minutes of the Pre-bid Conference

Dated June 16, 2014

The Addendum must be acknowledged on your lump sum bid.

The pre-bid conference for Request for Proposal for the Physics Building - Fire Alarm Replacement, Project 003-240915 was held on June 24, 2014, at 2:00 p. m. (local time) .  Robert Kuhn, Sr. Buyer,  reviewed the highlights of the pre-bid package, especially concerning details such as bid due dates and who vendors may contact during the live bid process.  Nancy Milstein and Hikmat Georges from MEP Engineers   discussed the technical aspects of the project and bid requirements, and conducted the Q & A session.

NOTE: You must have attended a pre-bid conference in order to be eligible to bid on a particular project.  Receipt of minutes or addenda without being at a pre-bid conference does not qualify your company to bid.

Numerous simple questions and answers were addressed at the pre-bid meeting. Some of the issues were as follows:

- A bid bond is not required for bids below $50,000.  Otherwise, a bid bond (5%) will be required for the full amount of the bid.

- Performance Bond and Material & Labor Payment Bond requirements are listed in the specifications of the job.  Performance & Material & Labor Payment Bonds must be provided by the awarded Vendor with the submission of the signed contract; which will then be submitted to FP&M management for counter signature.

- The awarded vendor must provide the required Certificate of Insurance in compliance with Section 800, article 11 of the bid specifications prior to commencement of any work.

- If your company has not previously done business with the University you may go to the Purchasing website at www.purchasing.wayne.edu and look for the “new vendor” link under “Information for Vendors” on the left.  You may submit a new vendor request form and an IRS form W-9.  This will register your company on our vendor list.  (NOTE: this does not replace the listserv.)

- This Project Requires the Contractor and any subcontractors to compensate all employees who come to the job site at no less than State of Michigan Prevailing Wage Rates.  A Prevailing Wage Rate Schedule is included in Section 00410 of the Bid Specifications.  Vendors must review these requirements to be sure they are in compliance with the requirements of the University and the State of Michigan. Contact the State of Michigan if further information on prevailing wage rate is needed at website http://www.michigan.gov/dleg/0,1607,7-154-27673_27706---,00.html.  Vendors must post wages at the job site in compliance with the complete Prevailing Wage Rate listing provided in Bid Documents.

- 1099 workers and subcontractors using 1099 workers are NOT acceptable

- Certified Payroll must be provided with each of the contractor’s pay applications for all workers who worked at the job site, in compliance with the State of Michigan policy.  Failure to provide certified payroll will constitute breach of contract and pay applications will be returned unpaid, and remain so until satisfactory supporting documents are provided.

- Signed waivers from all Subcontractors and suppliers must accompany Pay Applications or they will be returned for such documentation prior to approval.

- A properly executed sworn statement is required from all tiers of contractors, and sub-contractors indicating sub-contractors and suppliers which provide services or product of $1,000.00 or greater.  Sworn statements must accompany applications for payment

- All documents listed in the Front End Section 0410-2 “Wayne State Prevailing Wage Requirements” must accompany applications for payment. Failure to do so will result in the entire application package returned for correction.

- A checklist of all Pay Application requirements can be found in Section 00430-1.

- The competency and responsibility of Bidders will be considered in making the award.  The Owner does not obligate himself to accept the lowest or any other bids.  The Owner reserves the right to reject any and all bids and to waive any informalities in the Proposals

- Parking on WSU campus lots and structures are $6.50/access.  Vendor must build parking into their lump sum bid.

- Section 300, Form of Proposal has changed very recently, review carefully and complete in its entirety to avoid disqualification.

- The contractors must fill out our prequalification form.  They can attach additional information if they would like but at a minimum the information requested must be filled in on our form so that we do not have to hunt to find the information.

- Contractors who have withdrawn a bid after a University bid opening and/or refused to enter into a contract with the University upon notification of award within the last 3 years are not eligible to bid on this project.

- Project hours of operation are 7:00am – 5:00 pm.  Anything else requires advance notice and approval.

- Prequalification meeting will be held the first business day after bid openings.  Contractors must be available.  The Project Manager will coordinate the meetings.

- Prequalification meeting includes Schedule of Values from the Contractor, including a list of Contractor’s subcontractors and other qualifications required by the documents.

- An unsigned contract will be given to the successful Contractor at the conclusion of the Prequalification meeting, if all aspects of the bid are in order.  The Contractor has 5 business days to return the contract to the Project Manager for University counter signature.  The contractor must also submit a Performance Bond as outlined above and a Certificate of Insurance in the same 5 business day period.  In the event the Contractor fails to return the documents in this 5 day period, the University reserves the right to award the contract to the next most responsive bidder.

- An Optional second walk thru was not scheduled.  .

- Permit requirements are the responsibility of the awarded contractor as listed on Section 800 Article 4.

- Vendor must provide their own dumpster if needed, which must be rubber or plywood padded if placed on concrete.  Location and duration must be coordinated with the project manager.  Dumpster must be tagged with the name of your company clearly displayed. Any lawn damage must be restored.

- Questions are due by June 27, 2014  at 12:00 noon

- Bids are due no later than 2:00 p.m., July 8, 2014, at 5700 Cass Ave. Room 4200 AAB.  
No public bid opening will be held.

- Time of Completion: The Contract is expected to be fully executed on or about 15 calendar days after successful bidder qualification and recommendation of award.  The successful bidder (Contractor) agrees to start construction immediately after receipt of a fully executed contract and Purchase Order, and to complete the work as follows:  Substantial Completion, and State Approved Inspections (if appropriate), no later than October 31, 2014.

- A copy of the sign in sheet is available for downloading from the University Purchasing Web Site at  http://www.forms.purchasing.wayne.edu/Adv_bid/Adv_bid.html.

- This is an occupied area, awarded vendor must be considerate of environment (noise, cleanliness, etc)

Other:

- Building hours are 8:00 a. m. – 5:00 p. m. Earlier or “after hours” access to the building can be arranged.

- A loading dock is available, although it is not staffed.

- A freight elevator is available and is relatively large.

- State of Michigan Fire Marshal approval is not required as the Physics Building is not a classroom building.  University inspection by the Office of Risk Management is required.

- Fire alarms to be horns, not speakers.   System must be able to accommodate future notification system.

- Vendors are to take great care with removing spline ceiling as the University does not have any replacement tile stock. Vendors are responsible for ceiling removal and reinstallation and are cautioned to take appropriate care during removal of existing ceiling to retain material in good condition for reinstallation. Ceiling replacement per the Unit pricing for Acoustical Ceiling and grid system will be done only with the pre-approval of the university. New materials must comply with the university design standards (see item #21, below).

- The building will be fully occupied throughout the  construction time period, so there shall be no removal or

demolition of existing fire alarm systems until the new system is fully tested, inspected and approved by the Fire    Marshal.

- Vendor must coordinate with the project manager and building occupants for access to laboratory and office areas.   Work in research labs may involve work next to equipment or research activities that are sensitive to vibration and/or airborne particles, so adequate precautions must be taken. These details will be coordinated during a pre-construction kickoff meeting.

- Vendors must take measures to protect areas from dust, noise, vibrations, and etc. Vendors should assume that this may involve scaffolding and layers of protective plastic sheeting in research labs.  The cost of this protection is expected to be included in the vendor’s base bid.

Please note, room 342 is a “clean room” and requires special treatment/protection.  Special measures will be required to work in this space. Further information will be provided in a future addendum.

- Vendors can’t use existing conduit as they are already at capacity with wire.  When demolishing, Vendor must remove all wires back to the source.

- The basement mechanical rooms will require new duct smoke detectors, to be located to existing, and must include an automatic air handler “shut off” control.

- Smoke detectors adjacent to elevators are to remain.

- Any items/devices not on the drawings but discovered during the project must be identified and brought to the attention of the project manager.

- The boiler room is a detached building with wiring running underground to the basement of the Physics Building.   Vendor must provide new conduit as existing is filled to capacity.

- Wiring is to be installed in 2 different ways.  For corridors, wiring is to be above the ceiling.  In laboratories and offices, with standard ceilings, Vendor must use EMT conduit, surface mounted and painted to match existing wall finish.

- There are some available spare circuits in existing electrical panels.  However, if a panel is full and there are no further spare circuits, Vendor must install a new panel.  Panels are to be in the basement or on the 1st floor.

- Note: Work on the first floor needs to be completed prior to August 28 to avoid disturbing student activities.  Vendors must coordinate with the project manager.

- The University and FP & M Design Standards should be adhered to throughout this project.  The Design Standards can be accessed via the Purchasing website at www.procurement.wayne.edu or through the FP & M website, direct, through www.facilities.wayne.edu.

- Any requests to have specific manufacturers added to the “approved list” must be put in writing and emailed to Purchasing during the pre-bid question period.

- Materials staging will be available and is to be coordinated with the project manager during pre-construction kickoff meeting.

IMPORTANT- This is an addendum which MUST be acknowledged on your bid form

We will require two copies each of your lump sum proposals, vendor qualification questionnaire and your bid bond documents.

All questions concerning this project must be emailed to: Robert Kuhn, Procurement & Strategic Sourcing.  Email: ac6243@wayne.edu, and copy Valerie Kreher, Sr. Buyer, at rfpteam2@wayne.edu.

Do not contact either FP&M or the Design Firm directly as this may result in disqualification of your proposal.

Thank you for interest shown in working with Wayne State University.

Robert Kuhn

Senior Buyer

CC:	Nancy Milstein (Project Manager), Valerie Kreher, Sr. Buyer, Attendee list.