Division of Finance and Business Operations

Request for Proposal

# and Specifications for

RFP C & IT Air Conditioning and Maintenance\

Services 2013, Project R575373

No part of this publication may be reproduced, transmitted, transcribed,

stored in a retrieval system, or translated into any language in any form

by any means without the written permission of

Wayne State University

Wayne State University

Procurement & Strategic Sourcing

May 3, 2013

| Division of Finance and Business Operations |  | Procurement & Strategic Sourcing 5700 Cass Avenue, suite 4200 Detroit, Michigan 48202 (313) 577-3734 FAX (313) 577-3747 |
| --- | --- | --- |

May 3, 2013

Dear Vendors:

IMPORTANT – PLEASE NOTE:  Bid notices will be sent only to those Vendors registered to receive them via our Bid Opportunities Listserve service.  To register, to

http://www.forms.purchasing.wayne.edu/Adv_bid/Adv_bid.html, and click on the “Join our Listserve” link at the top of the page.  Instructions are at the top of the page, and the None – by Invitation Listserv service is under “Service Bid Opportunities”.

Wayne State University invites you to participate in its Request for Proposal process to provide HVAC/Air Conditioning Services, on a “turn-key” basis, for the C & IT Department, per the specifications contained herein the Request for Proposal.  This service is expected to commence on July 1, 2013.

We have a bid information package complete with the Request for Proposal and complete specifications available for downloading from the University Purchasing Web Site at

http://www.forms.purchasing.wayne.edu/Adv_bid/Adv_bid.html (include capitalization and underscores) as of May 3, 2013.  When visiting the Web Site, click on the “Service

” link in green.  Copies of the RFP will not be available at the pre-proposal meeting.  If you are interested in participating in this process, you and/or responsible representatives of your organization must attend our mandatory pre-proposal meeting to be held on:

May 9, 2013, 9:00 - 10:00 a.m.

C & IT DEPARTMENT

5925 Woodward,

(Main Lobby)

Detroit, MI  48202

For your convenience a map of the University and appropriate parking lots can be downloaded and printed from: http://campusmap.wayne.edu/ .  Guest parking in any of the University student and guest lots is $6.00.  A detailed list of Cash & Coin operated lots can be viewed at

http://purchasing.wayne.edu/cash_and_credit_card_lots.php .  Cash lots dispense change in quarters.  Due to time constraints, Vendors are encouraged to avoid parking at meters on the street (especially blue “handicapped” meters).  Please confirm your attendance at the mandatory pre-proposal meeting by faxing your intent to participate (or not to participate) by using Appendix 2 to Ms. Pat Milewski at (313) 577-3747 no later than noon on May 8, 2013.

We hope to see you at the mandatory pre-bid meeting.  Please bring a copy of this Request for Proposal for your reference during the meeting.  Should you have any questions or concerns about this invitation, please contact me at (313) 577–3712, or email: ac6243@wayne.edu.  Thank you for your interest in doing business with Wayne State University.

Sincerely,

Robert Kuhn, Sr. Buyer,

Senior Buyer

Enclosure

Cc:  Ken Doherty, Valerie Kreher, Jerry Nechal, Larry Bott

## RFP:  C & IT Air Conditioning and Maintenance Services 2013,

## Project R575373

Note										ii

I.	Introduction	1

II.	Information for VENDOR	1

A.	General	1, 2

B.	Calendar of Events	2

C.	Mandatory Pre-Proposal Meeting	3

D.	Examination of the Request for Proposal	3

E.	Delivery of Proposals	3, 4

F.	Proposal Format	4

G.	Proposal Evaluation	4, 5

H.	VENDOR Profile, Experience, References and Lost Accounts	5, 6

III.	Scope of Work and Technical Requirements	13-16

IV.	General Requirements and Guidelines	6

SCHEDULES

Schedule A       Proposal Certification, Non-Collusion Affidavit, VENDOR Acknowledgements

Schedule B,      Insurance Requirements

Schedule C,      Cost Schedule

Schedule D,      Summary Questionnaire

EXHIBITS TO BE SUBMITTED WITH VENDOR PROPOSAL(S)

VENDOR Exhibit 1,  Exceptions / Restricted Services

VENDOR Exhibit 2,  Profile/Experience/References

VENDOR Exhibit 3,  Service Plan

VENDOR Exhibit 4,  Sample Management Reports

APPENDICES

Appendix 1, Wayne State University Map – (see website: http://campusmap.wayne.edu )

Appendix 2,  Registration/Intent Form

Appendix 3,  Prevailing Wage Rate Schedules – Not Applicable

Appendix 4,  Equipment List at C & IT 5925 Woodward

Appendix 5,  Equipment List at C & IT Fiber Rooms Throughout the Campus

Appendix 6,  Equipment List at the Oakland Center

ATTACHMENTS

Attachment A   Annual Maintenance Requirements at C & IT 5925 Woodward Avenue, Detroit, MI

Attachment B    Maintenance Requirements at C & IT Fiber Rooms Throughout WSU Campus

Attachment C    Bi – Annual Maintenance requirements at Disaster

Recovery Site at the WSU Oakland Center

Attachment D  Wayne State University Service Provider Agreement

I.	INTRODUCTION

A. 	Wayne State University (hereafter referred to as UNIVERSITY) is a national research university with an urban teaching and service mission.  It is a constitutionally autonomous public university with 13 schools and colleges, has an enrollment of approximately 29,000 students, and has an alumni roster of over 230,000. The graduate school, with nearly 13,000 students, is the largest in Michigan.  It is one of 2.2 percent of all colleges and universities, nationwide, to hold the prestigious Carnegie Doctoral Extensive designation. WSU is one of the approximately 150 universities nationwide that hold this status.

B.	Procurement & Strategic Sourcing is soliciting proposals from qualified professional organizations, hereafter referred to as VENDOR(s), who specialize in providing Air Conditioning Service and Maintenance of superior quality, at competitive pricing, as described in the Statement of Work section of the Request For Proposal (RFP).   The University is seeking a three year agreement with a single vendor with the option to renew for 2 additional twelve (12) month periods, per the following:

Initial Contract Period – Pricing to be Firm and Fixed

July 1, 2013 – September 30, 2013

October 1, 2013 – September 30, 2014

October 1, 2014 – September 30, 2015

Additional Optional Twelve Month Periods

October 1, 2015 – September 30, 2016

October 1, 2016 – September 30, 2017

The Project must commence on or before July 1, 2013.  .

This RFP outlines basic requirements as specified in the Scope of Work section of the RFP (Section IV).  Proposals submitted are to be in accordance with the outline and specifications contained herein and are to remain in effect a minimum of 120 days from the date of submission, and may be subject to further extensions as negotiated.

C.	The UNIVERSITY reserves the right to accept, reject, modify, and/or negotiate any and all proposals received in conjunction with the RFP.  It reserves the right to waive any defect or informality in the Proposals on the basis of what it considers to be in its best interests.  Any proposal may be rejected which the UNIVERSITY determines to be incomplete, conditional, obscure, or has irregularities of any kind.  The UNIVERSITY reserves the right to award to the firm, or firms, which in its sole judgment, will best serve its long-term interest.

This RFP in no manner obligates the UNIVERSITY to the eventual purchase of any products or services described, implied, or which may be proposed, until confirmed by written agreement, and may be terminated by the UNIVERSITY without penalty or obligation at any time prior to the signing of an Agreement or Purchase Order.

D.	Expenses for developing and presenting proposals shall be the entire responsibility of the VENDOR and shall not be chargeable to the UNIVERSITY.  All supporting documentation and manuals submitted with this proposal will become the property of the UNIVERSITY.

E.	All questions concerning this Request for Proposal are to be directed to Robert Kuhn, Sr. Buyer, Senior Buyer, Email; ac6243@wayne.edu and to Valerie Kreher, Senior Buyer, Email; rfpteam2@wayne.edu@wayne.edu.  Copy both Robert Kuhn, Sr. Buyer, and Valerie Kreher, Sr. Buyer, on all E-Mail questions.  The deadline for questions is

May 20, 2013, 12:00 noon.  Under no circumstances may a VENDOR contact other individuals at the UNIVERSITY, or its consultants to discuss any aspect of this RFP, unless expressly authorized by Procurement & Strategic Sourcing to do so.

II.	INFORMATION FOR VENDOR

A.	General

This RFP contains requests for information.  VENDORS, however, in responding to this RFP, are encouraged to provide any additional information they believe relevant.

VENDORS are encouraged to examine all sections of this RFP carefully, in that the degree of interrelationship between sections is high.  Whenever the terms "must", "shall", "will", "is required", or "are required" are used in the RFP, the subject being referred to is to be a required feature of this RFP.

B.	Calendar of Events

| Activity____________ Formal Release of RFP | Responsibility ___ Purchasing (PD) | Date____ May 3, 2013 |
| --- | --- | --- |
| Mandatory Prebid meeting at the C & IT DEPARTMENT, 5925 Woodward, (Main Lobby), Detroit, MI 48202 (Site Visits to be scheduled at the pre-bid) | PD/Evaluation Team (ET)/VENDORS | May 9, 2013 9:00 - 10:00 a.m. |
| Questions due to Procurement & Strategic Sourcing | VENDORS | May 20, 2013 - 12 Noon |
| Delivery of Proposals to the Academic/ Administration Bldg., Purchasing Dept., 5700 Cass Avenue, 4th Floor – Suite 4200, Detroit, MI | VENDORS | May 23, 2013 by 4:00 p.m. |
| Evaluation of Proposals (clarifications & negotiations) | PD/ET | Week of May 24, 2013 |
| Announcement of Selected VENDOR | PD | Week of June 1, 2013 |
| Readiness for Service/Contract Commencement | VENDORS | Week of July 1, 2013 |
| Project Completion | VENDORS/ET | June 31, 2014 |

The UNIVERSITY will make every effort to adhere to the above schedule.  It is subject however, to time extensions at the University’s discretion.

C.	Mandatory Pre-Proposal Meeting

You must attend a mandatory Pre-Proposal Meeting on May 9, 2013 at 9:00 - 10:00 a.m.  at the C & IT DEPARTMENT, 5925 Woodward, (Main Lobby), Detroit, MI  48202, as a condition for submitting a proposal.

Pre-registration for the meeting is to be made on or before Noon on, May 8, 2013.  Please fax Appendix 2 to attention Ms. Pat Milewski at (313) 577–3747 to confirm your attendance.

During this meeting, we will answer any questions you may have to clarify any ambiguities in this Request for Proposal.  Answers to questions that cannot be answered during this meeting will be emailed to all VENDORS and posted to the University website as soon as they are obtained.

D.	Examination of the Request for Proposal

Before submitting proposals, each VENDOR will be held to have examined the UNIVERSITY requirements outlined in the Scope of Work and Technical Information sections, and satisfied itself as to the existing conditions under which it will be obligated to perform in accordance with specifications of this RFP.

No claim for additional compensation will be allowed due to unfamiliarity with the specifications and/or existing conditions.  It shall be understood that the VENDOR has full knowledge of all of the existing conditions, and accepts them "as is."

E.  	Delivery of Proposals (10-30-2009)

An original (clearly marked as such) plus one copy (2 total) of concise proposals in booklet or notebook form with supporting documentation shall be delivered in a sealed envelope or container to UNIVERSITY Procurement & Strategic Sourcing.

In addition, an electronic version is required, which should be submitted to our secure mailbox at rfp@wayne.edu and be sure your subject line reads “(company name) RFP C & IT Air Conditioning and Maintenance Services 2013, Project R575373 Response”. The electronic submission should be limited to no more than one of each of the following file types:  1 Word Document and/or 1 Excel Workbook and/or 1 PDF document, with a total file size less than 20 megabytes.  If your submission was sent correctly, you will receive an auto-reply message acknowledging receipt of your Proposal.  If you do not receive an auto-reply message, check the address you used and resubmit your Proposal.  However, in the event a discrepancy exists between the electronic submission and the original copy of the Vendor’s Response Proposal, the original copy will prevail.

Please note – Your RFP submission is not valid unless we receive both the hard copy and the electronic copy on or before the due date and time.

The specific format for responses is detailed in Section II F (below).  Proposals and Schedule C, Cost Schedule must be signed and the authority of the individual signing must be stated thereon. All responses are to be addressed to:

ATTN.: Robert Kuhn, Sr. Buyer,  Senior Buyer

Wayne State University

## RFP:  C & IT Air Conditioning and Maintenance Services 2013,

## Project R575373

5700 Cass Avenue, 4th Floor - Suite 4200 AAB

Detroit, MI   48202

And:  E-mail a copy to RFP@wayne.edu /

subject line: “(company name) RFP C & IT Air Conditioning and Maintenance Services 2013, Project R575373 Response”.

Deadline for receipt of proposals by Procurement & Strategic Sourcing is, May 23, 2013 by 4:00 p.m. (local time).  Date and time will be stamped on the proposals by Procurement & Strategic Sourcing.  Proposals received after that time will not be accepted.  No details of the proposal will be divulged at the time of opening.

F.	Proposal Format

Proposals are to be submitted in notebook form with appropriate indices.  Each proposal should provide a straightforward concise description of the VENDOR'S service, approach and ability to meet the UNIVERSITY'S needs as stated in this RFP.  Schedules and Exhibits listed below must be included in your proposal:

Schedules (provided in this package)

Schedule A - 	Proposal Certification, Non Collusion Affidavit, VENDOR Acknowledgements

Schedule B  -	Insurance Requirements

Schedule C  -    Cost Schedule, Summary of Quoted Rates

Schedule D  -    Summary Questionnaire

Exhibits (created by Vendors as needed)

Exhibit  1     -	 Exceptions/Restrictions;  if any  (Section II G)

Exhibit  2     -	 Profile/Experience/References  (Section II H)

Exhibit  3     -   	 VENDOR Service Plan (Section III)

Attachments (provided in this package)

Care should be exercised in preparation of the proposals since it is the UNIVERSITY'S intent to have the final contract documentation consist of the RFP, VENDOR Proposal, any letters of clarification, and a one or two page enabling Signatory Document and/or Purchase Order.

Unnecessarily elaborate brochures or other presentations beyond those sufficient to present a complete and effective quotation are not desired.

G.	Proposal Evaluation

- Proposals will be evaluated and award will be based on the VENDOR'S ability to offer the best value (quality, past performance and price), and on anticipated quality of service.  Items considered include but are not limited to:

Ability to meet all mandatory requirements and specifications of this RFP;

Cost of Services; Compensation and Fees; (Schedule C);

Financial Strength of the VENDOR;

Proposal Documentation / Presentation;

VENDOR'S Experience (Exhibit 2);

VENDOR Profiles/References; (Exhibit 2);

VENDOR Service Plan; (Exhibit 3);

NOTE:   Evaluation Criteria are in alphabetical order and are not stated in order of preference.

VENDOR proposals will be evaluated by a team consisting of members of the UNIVERSITY'S Purchasing and C & IT Department.  A preliminary screening will be used to identify competitive VENDORS who have met the mandatory requirements.  Procurement & Strategic Sourcing may subsequently request selected VENDORS to make a presentation at a set time and date, to clarify information provided in the proposals.  Final consideration, evaluation, and recommendation may be made at this point.  However, the UNIVERSITY reserves the right to take additional time for reference review, site visits and/or proposal negotiations.

2.	To qualify for evaluation, a VENDOR'S proposal must be responsive, must have been submitted on time and must materially satisfy all mandatory requirements identified throughout the RFP, in the judgment of the UNIVERSITY.  Any deviation from requirements indicated herein must be stated in the proposal specifically under the category "Restricted Services", and clearly identified as Exhibit 1.  Otherwise it will be considered that proposals are in strict compliance with all requirements.  Check the box indicating "None" for Restricted Services on the Proposal Certification Schedule A.  In those cases where mandatory requirements are stated, material failure to meet those requirements may result in disqualification of the VENDOR'S response

3.   If there are portions of any proposal the UNIVERSITY finds unacceptable or otherwise in need of clarification or revision, the UNIVERSITY reserves the right to clarify or negotiate with any or all VENDORS.  Should the outcome of evaluations result in a recommendation, any resulting contract will be subject to the approval of the UNIVERSITY'S General Counsel and must be approved and signed by the appropriate UNIVERSITY representative.

- After notification of acceptance of proposal and the signing of a resulting agreement and/or Purchase Order, the successful VENDOR will be expected to establish and be in a position to commence work or services on or before July 1, 2013.

H.	VENDOR Profile, Experience, References, and Lost Accounts

1.	VENDOR Profile should include:

VENDOR is required to provide organizational data that demonstrates the size, scope and capability of the Company to handle the UNIVERSITY'S specific requirements specified in this RFP.  Explain any company relationships that could be construed to be a conflict of interest in doing business with the UNIVERSITY now or in the future.

Upon University request, VENDOR must agree to provide independently audited financial statements including its statement of financial position, statement of operations, and statement of cash flows for at least the past three years.  Vendor must further agree to permit the UNIVERSITY, upon request, to audit VENDOR's books as related to the Wayne State University account.

Failure to agree to this will result in disqualification of your bid (see Schedule D).

Financial Information will be treated as confidential and not added to the publicly permanent RFP file.  Requested Financials must be sent to:

ATTN.: Kenneth Doherty, Assistant Vice President

Procurement & Strategic Sourcing

Wayne State University

## RFP:  C & IT Air Conditioning and Maintenance Services 2013,

## Project R575373

Procurement & Strategic Sourcing

5700 Cass Avenue, 4th Floor - Suite 4200 AAB

Detroit, MI   48202

VENDORS must include a self-addressed envelope marked "Confidential" with their financial statement. Statements will be returned upon completion of any University review.

2.	Experience

VENDORS are to state in their proposals their qualifications to meet the RFP specifications in terms of past and current consulting experience with the same or similar requirements.  This information should be provided in the VENDOR’S Exhibit 2 of their proposal.  VENDORS are to focus on experiences with organizations having needs similar to that of the UNIVERSITY.

3.	References

Upon request, VENDOR must agree to provide a minimum of three (3) qualified references.  Requests for references will come from Robert Kuhn, Sr. Buyer, , Senior Buyer, and will be treated as confidential and not added to the publicly permanent RFP file.

References are to be from organizations that have successfully utilized the products and services.  The references supplied should include the name and address of the organization, and the contact name(s), titles, e-mail, and the telephone numbers.

Failure to agree to this will result in disqualification of your bid (see Schedule D).

4.	Lost Accounts and Legal Actions

Upon request, VENDOR must agree to provide a list of significant accounts that the VENDOR has lost during the past three (3) years.  "Significant" for this purpose shall be construed to mean accounts representing billings by the VENDOR in the range of $25,000.00 or more each year.  A lost account can be defined when the vendor has been terminated on a job because of performance or default.  Contact names and telephone numbers of affected Companies must be provided.

Indicate any significant past or pending lawsuits or malpractice claims against the VENDOR.

I.	VENDOR Service Plan

Vendors should include a complete description of the products and services offered in their Proposal. The Service Plan should include, but not be limit to:

- A summary of the products or services to be provided.

- When applicable, a timeline showing how the Vendor plans to deliver products and/or services to fulfill any contract issued as a result of this RFP.

- Key staff members at the Vendors organization that will be assigned to the University account or will otherwise be part of an implementation team.

- Any resource requirements on the part of the University necessary in order for the Vendor to meet its obligations under an agreement resulting from this RFP.

- Any hardware, software, or other technology the University must have in order to use the Vendors products or services.

- Any alternative ideas or proposals that should be considered by the University in addition to the base proposal.

III.	SCOPE OF WORK AND TECHNICAL REQUIREMENTS

The Purchasing (PD) Department of the UNIVERSITY is soliciting proposals from qualified professional organizations, hereafter referred to as VENDOR(s), to provide for Air Conditioning & Maintenance Services for the C&IT Department, communications closets located throughout the UNIVERSITY, and the Disaster Recovery Site (located at the University’s Oakland Center – 12 Mile and Farmington Road).  Pricing is to be provided for each section separately, as shown on Schedule C, Cost Schedule.  The contract will be for three years, with the UNIVERSITY having the option to renew for up to 2 one-year periods, through the 2018 season.  The UNIVERSITY reserves the right to award each portion separately.

The successful VENDOR(S) will be responsible for all services at the referenced locations, and agrees to provide all necessary labor, equipment, and materials necessary to maintain the specified areas in a safe condition. This shall include the use of proper knowledge, skills, materials, and equipment on a timely basis.  VENDOR(S) will also provide the supervision and management necessary to complete these services in a timely and efficient manner.

VENDOR understands that performance level and fulfillment of the contract will be monitored by the UNIVERSITY on an on-going basis.  The successful VENDOR(S) must make personal contact with the Computing & Information Systems Department on a regular basis to discuss the services provided, satisfaction with services provided, and any other necessary business.

The VENDOR shall submit a quality assurance program for review and approval by the UNIVERSITY.

The successful VENDOR(S) shall be responsible for the negligent damage caused by the VENDOR, its employees and/or agents to buildings and other property belonging to the UNIVERSITY.

VENDORS must submit proof of insurance as outlined in Section III, W "Insurance Requirements" and in Schedule B.  In addition, the VENDOR must provide any special riders appropriate for Air Conditioning & Maintenance Services, should the VENDOR be awarded the contract.

Failure to include these items in your proposal may cause the proposal to be considered non-responsive and be disqualified.

Section 1

SCOPE OF AGREEMENT FOR C&IT BUILDING AT 5925 WOODWARD

- Contractor will agree that all work will be performed by qualified licensed Journeyman Refrigeration Mechanics.

- Contractor will agree to maintain a record of refrigerant usage on each piece of equipment and provide a copy to Wayne State C&IT Facilities department due annually on September 30th.

- Contractor will maintain a record of all work performed to each piece of equipment covered under contract and provide an electronic copy to Wayne State C&IT Facilities department due annually on September 30th.

    - Work sheets detailing work performed and hours worked will be turned in to Wayne State C&IT Facilities department at the end of each work day. Upon completion of each assignment or repair a summary work sheet will be submitted detailing the required repairs.  This will include a detailed copy of the maintenance inspection checklist for the required maintenance on each piece of equipment.

    - Contract will include parts and materials including replacement compressors.

    - Contract will include labor during designated hours of 8:00 am to 4:30 pm Monday-Friday.

- Contractor will agree to provide emergency call number and service within 4 hours of call.

- Contractor will agree to provide service within 24 hours of call unless otherwise agreed with Wayne State C&IT Facilities department.

- Contractor will schedule maintenance visits to assure periodic maintenance for inspections, coil cleaning and filter changes on a quarterly basis.

- Contractor will agree to perform condenser and dry-cooler maintenance after May 1st and no later than June 5th of each year. This work will require the application of a nickel safe foam type coil cleaning agent followed by a clean water rinse with a pressure washer.

Section 2

SCOPE OF AGREEMENT FOR C&IT FIBER ROOMS THROUGHOUT WAYNE STATE UNIVERSITY CAMPUS

- Contractor will agree that all work will be performed by qualified licensed Journeyman Refrigeration Mechanics.

- Contractor will agree to maintain a record of refrigerant usage on each piece of equipment and provide a copy to Wayne State C&IT Facilities department due annually on September 30th.

- Contractor will maintain a record of all work performed to each piece of equipment covered under contract and provide a copy to Wayne State C&IT Facilities department due annually on September 30th.

    - Work sheets detailing work performed and hours worked will be turned in to Wayne State C&IT Facilities department at the end of each work day. Upon completion of each assignment or repair a summary work sheet will be submitted detailing the required repairs.  This will include a detailed copy of the maintenance inspection checklist for the required maintenance on each piece of equipment.

    - Contract will provide labor rate for services during designated hours of 8:00 am to 4:30 pm Monday-Friday.

    - Service work will be billed time and material.

    - Contract will provide labor rate for emergency service outside of normal hours designated above.

    - Emergency service will be billed as time and material

- Contractor will agree to provide emergency service within 4 hours of call.

- Contractor will agree to provide service within 24 hours of call unless otherwise agreed with Wayne State C&IT Facilities department.

- Contract will indicate a fixed price for completion of the annual maintenance detailed on attachment C for all equipment listed on attachment D.   This fixed price will be figured as an average annual maintenance cost per unit so that future installations can be added if need arises.

- Contractor will schedule one annual maintenance visit for each air conditioning unit to assure periodic maintenance is completed no earlier than April 1st and prior to June 5th of each year.

- Contractor will agree to perform condenser and dry-cooler maintenance and cleaning after April 15th and no later than June 5th of each year.

- Contract will identify cost mark-up on repair parts in percentage terms, verifiable on request of Wayne State University C&IT Facilities department.  Wayne State University C&IT Facilities department will accept supplier invoice as proof.

Section 3

SCOPE OF AGREEMENT FOR DISASTER RECOVERY SITE AT WAYNE STATE UNIVERSITY OAKLAND CAMPUS

- Contractor will agree that all work will be performed by qualified licensed Journeyman Refrigeration Mechanics.

- Contractor will agree to maintain a record of refrigerant usage and provide a copy to Wayne State C&IT Facilities department due annually on September 30th.

- Contractor will maintain a record of all work performed to each piece of equipment covered under contract and provide a copy to Wayne State C&IT Facilities department due annually on September 30th.

    - Work sheets detailing work performed and hours worked will be turned in to Wayne State C&IT Facilities department upon completion of each assignment or repair.

    - Contract will provide labor rate for services during designated hours of 8:00 am to 4:30 pm Monday-Friday.

    - Service work will be billed time and material.

    - Contract will provide labor rate for emergency service outside of normal hours designated above.

    - Emergency service will be billed as time and material

- Contractor will agree to provide emergency service within 4 hours of call.

- Contractor will agree to provide service within 24 hours of call unless otherwise agreed with Wayne State C&IT Facilities department.

- Contract will indicate a fixed price for completion of the annual maintenance detailed on attachment E for all equipment listed on attachment F.

    - Contractor will schedule one annual maintenance visit for each air conditioning unit to assure periodic maintenance is completed no earlier than April 1st and prior to June 5th of each year.

- Contractor will agree to perform condenser maintenance and cleaning after April 15th and no later than June 5th of each year.

- Contract will identify cost mark-up on repair parts in percentage terms, verifiable on request of Wayne State University C&IT Facilities department.  Wayne State University C&IT Facilities department will accept supplier invoice as proof.

A.	Terms and Conditions   (2-23-2009)

The Proposal response must include a formal copy of any VENDOR'S terms and conditions applicable to this transaction. Evaluation and acceptance and/or modification of these terms and conditions by the University's General Counsel is essential prior to the award of the contract.  If supplied, this should be included in Exhibit 1 of the Vendor’s proposal.  In the event the VENDOR does not supply terms and conditions with their proposal, the University's terms and conditions will govern this transaction.

B.	Governing Law  (Michigan)

VENDOR agrees that, in the event of a dispute, laws of the State of Michigan will prevail.

C.	Non-Discrimination

The parties agree that in the performance of any contract they shall not discriminate in any manner on the basis of race, creed, color, national origin, age, religion, sex, sexual orientation, marital status or handicap protected by law.  Such action shall include, but is not limited to the following:  employment, upgrading, demotion, transfer, recruitment or recruitment advertising; layoff or termination; rates of pay or other forms of compensation.  By submitting a proposal, VENDORS certify that they will conform to the provisions of the Federal Civil Rights Action of 1964, as amended.  Information on the Civil Rights Act can be found at http://www.eeoc.gov/laws/statutes/titlevii.cfm

D.	Civil Rights Requirements

All VENDORS must be in compliance with the directives of the Michigan Department of Civil Rights.  The Department of Civil Rights web address is

http://www.michigan.gov/mdcs/0,1607,7-147-6881---,00.html

D.	Immigration Reform and Control Act of 1986

By submitting a proposal, the VENDORS certify that they do not and will not during the performance of this contract employ illegal alien workers or otherwise violate the provisions of the federal Immigration Reform and Control Act of 1986.

E.	Debarment Status   (6-12-2009)

By submitting a proposal, VENDORS certify that they are not currently debarred from submitting bids on contracts nor are they an agent of any person or entity that is currently debarred from submitting bids on contracts.  The University’s Department Policy can be found at http://purchasing.wayne.edu/vendors/debarred.php. State of Michigan information on Debarment can be found at

http://www.michigan.gov/buymichiganfirst/0,1607,7-225-48677-20042--,00.html. The Federal Debarred Vendor List   (Excluded Parties List System) and related links can be found at http://www.epls.gov/

F.	Indemnification and Hold Harmless

The VENDOR shall defend, indemnify and hold harmless the UNIVERSITY, its officers, employees and agents, against any and all liability of whatever nature which may arise directly or indirectly by reason of the VENDOR'S performance under this Agreement.

G.	VENDOR Liability

The VENDOR will be liable for any associated costs of repairs for damage to buildings or other UNIVERSITY property caused by the negligence of the VENDOR'S employees.

H.	Early Termination by the University

The UNIVERSITY shall have the right to terminate the contract with the VENDOR without penalty after the UNIVERSITY'S thirty (30) days written notice of termination to the VENDOR under the following circumstances:

1.	Default of VENDOR

It shall be considered a default whenever the VENDOR shall:

a.	Disregard or violate material provisions of the contract documents or UNIVERSITY instructions, or fail to execute the work according to the agreed upon schedule of completion and/or time of completion specified, including extensions thereof, or fail to reach agreed upon performance results.

- Declare bankruptcy, become insolvent, or assign company assets for the benefit of creditors.

2.	Convenience of the UNIVERSITY

When termination of the contract services is construed by the UNIVERSITY to be in its best interest for serving the community and its students, faculty, and staff.

Note:  Any contract cancellation notice shall not relieve the VENDOR of the obligation to deliver and/or perform prior to the effective date of cancellation.

I.	Cancellation of Contract by VENDOR

VENDOR must provide a minimum of ninety (90) days written notice of cancellation of contract to the UNIVERSITY regardless of the reason for said termination.  Such notification must be sent to:

Kenneth Doherty,  Assistant Vice President

## Procurement & Strategic Sourcing

Wayne State University

## RFP:  C & IT Air Conditioning and Maintenance Services 2013, Project R575373

5700 Cass Avenue, Suite 4200, A.A.B.

Detroit, MI  48202

J.	Joint or Partnering Bids/Proposals

A joint bid/proposal by two or more Vendors proposing to participate jointly in performance of proposed work may be submitted.  A single Vendor must be clearly identified as the “Primary Vendor” who will assume responsibility for performance of all other Vendors and all subcontractors.  The Primary Vendor must identify itself as such and submit the proposal under its company name and signature.  If a contract is awarded in response to a joint bid/proposal, the Primary Vendor must execute the contract and all Partner Vendors must verify in writing that the Primary Vendor is authorized to represent them in all matters relating to the contract.  At least one of the Vendors must have attended any and all mandatory Pre-Proposal or other meetings.

K.	Non-Assignment

The agreement shall be between the UNIVERSITY and the VENDOR and the VENDOR shall neither assign nor delegate the agreement, its rights or obligations, or any of its terms without the express written permission of the UNIVERSITY.

L.	Price Schedules

VENDOR is to quote the products and services in accordance with specifications set forth in this Request for Proposal.  Prices and other requested data must be stated on or in the exact format of Cost Schedule C.  Vendors must not modify the format of any Price Schedule or to alter its functionality.

Please Note:	You must respond using Schedule C.  Failure to do so may result in disqualification of your Proposal.  VENDOR shall be responsible for all errors and omissions.

A copy of Cost Schedule C is to be provided in Excel format with your electronic submission.  The paper copy will govern if any discrepancies exist between the paper copy and electronic version.

M.	Pricing Variances

No changes shall be made, nor invoices paid for extra changes, alterations, modifications, deviations, and extra orders except upon a written change order from the UNIVERSITY.  The UNIVERSITY will not authorize payment for changes, alterations, modifications, deviations, etc. that are a result of VENDOR error.

O.	Certification, Affidavit, and Acknowledgements (11-01-11)

The Proposal Certification, Non-Collusion Affidavit, and Vendor Acknowledgements, Schedule A, must be executed as a part of the VENDOR'S proposal.

P.	VENDOR Payment/Billing Terms

Payments of invoices will be made thirty (30) days after receipt and approval of invoice, by the UNIVERSITY, for each month completed.

ACH payments are both faster and less costly for Vendors and the University.  As a result, this is the University’s preferred payment method.  To enroll in the University’s ACH program, visit http://fisops.wayne.edu/disbursements/tax-forms.php and download the ACH payment agreement form.  The completed form should be signed and sent to vendorach@wayne.edu.

Q.	Entire Agreement

An agreement, when fully executed, shall incorporate by reference this RFP and the Vendor’s response Proposal, and will contain all the covenants and agreements between the parties with respect to the subject matter of this agreement.  Any amendment or modification to this agreement must be in writing and signed by all parties.

R.	Severability

It is understood and agreed that if any part, term, or provision of this agreement is held to be illegal or in conflict with any law of the State of Michigan, the validity of the remaining portions or provisions shall be construed and enforced as if the Agreement did not contain the particular part, term, or provision held to be invalid.

S.	Modification of Service

The UNIVERSITY reserves the right to modify the services during the course of the contract, with concurrence of the VENDOR.  Any changes in pricing and rates proposed by the VENDOR resulting from such changes are subject to acceptance by the UNIVERSITY.

In the event prices and rates cannot be negotiated to the satisfaction of both parties, the contract may be subject to cancellation and competitive bidding based upon the new specifications.

T.	Publicity

VENDORS must refrain from giving any reference to this project, whether in the form of press releases, brochures, photographic coverage, or verbal announcements, without written approval from the UNIVERSITY.

U.	Independent Contractor

The VENDOR agrees that in all respects its relationship with the UNIVERSITY will be that of an independent contractor.  Vendor will not act or represent that it is acting as an agent of the UNIVERSITY or incur any obligation on the part of the UNIVERSITY without written authority of the UNIVERSITY.

V.	Confidentiality

Proposals could be subject to public review after the contracts have been awarded.  VENDORS responding to this proposal are cautioned not to include any proprietary information as part of their proposal unless such proprietary information is carefully identified as such in writing, and the UNIVERSITY accepts, in writing, the information as proprietary.

W.	Insurance Requirements (10-5-2009)

VENDORS must provide Certificates of Insurance or other evidence that insurance is in place.  If awarded a contract, VENDOR must then provide a Certificate of Insurance naming Wayne State University / Office of Risk Management as a certificate holder and the Board of Governors as an additional insured.  During the life of the contract, the VENDOR must maintain insurance as stated in Insurance Provisions (Schedule B) and any additional requirements as specified by the UNIVERSITY Office of Risk Management.

X.	Minority, Woman and Disabled Veteran Owned Business Enterprises (M/W/DBEs)

Specify in your proposal whether ownership of your company is a certified M/W/DVBE.  The University, in accordance with guidelines from the MMSDC and WBENC, considers a M/W/DVBE as one that is at least 51% owned, operated, and controlled by a M/W/DVBE, or in case of a publicly-owned business, at least 51% of the stock must be owned by a M/W/DVBE.

If the firm is not a M/W/DVBE, describe the firm’s partnering relationships (if any) with M/W/DBE and how it plans to support the UNIVERSITY’S goal to award UNIVERSITY business to M/W/DVBEs.

1.	Reporting

The selected firm will identify and fairly consider M/W/DVBE for subcontracting opportunities when qualified firms are available to perform a given task in performing for the UNIVERSITY under the resulting agreement.  The selected VENDOR must submit a quarterly M/W/DVBE business report to the UNIVERSITY Procurement & Strategic Sourcing by the 15th of the month following each calendar quarter; specifically the months of April, July, October, and January.  Such reports should be sent directly to:

Kenneth Doherty,  Assistant Vice President

## Procurement & Strategic Sourcing

Wayne State University

## RFP:  C & IT Air Conditioning and Maintenance Services 2013, Project R575373

5700 Cass Avenue, Suite 4200, A.A.B.

Detroit, MI  48202

2.	Report Detail

M/W/DVBE business reports must contain, but are not limited to the following:

- Firm’s name, address, and phone number with which the VENDOR has contracted over the specified quarterly period

- Contact person at the minority firm who has knowledge of the specified information

- Type of goods and/or services provided over the specified period of time

- Total amount paid to the minority firm as it relates to the UNIVERSITY account.

Specify in your proposal whether your company is a certified 8(A) firm.

A complete set of the University's Supplier Diversity Program, which includes complete definitions of each of the above, can be downloaded from our web site at

http://purchasing.wayne.edu/docs/university_policy_2004_02.doc.

Y.	Ownership of Documents

All documents prepared by the VENDOR, including but not limited to: tracings, drawings, estimates, specifications, field notes, investigations, studies and reports, shall become the property of the UNIVERSITY.  At the UNIVERSITY’S option, such documents will be delivered to UNIVERSITY Procurement & Strategic Sourcing. Prior to completion of the contracted services, the UNIVERSITY shall have a recognized proprietary interest in the work product of the VENDOR.

Z. 	Prevailing Wage Rates   (4-25-2010)

Wayne State University requires all project contractors, including subcontractors, who provide labor on University projects to compensate at a rate no less than prevailing wage rates.

The rates of wages and fringe benefits to be paid to each class of laborers and mechanics by each VENDOR and subcontractor(s) (if any) shall be not less than the wage and fringe benefit rates prevailing in Wayne County, Michigan, as determined by the United States Secretary of Labor.  Individually contracted labor commonly referred to as “1099 Workers” are not acceptable for work related to this project.

Installers of furniture or equipment responsible for onsite assembly must be classified minimally as carpenters, and those responsible for electrical connections must be classified minimally as electricians.

Additional information can be found on University Procurement & Strategic Sourcing’s web site at purchasing.wayne.edu under Information for Vendors.

If you have any questions, or require rates for additional classifications, please contact:

Michigan Department of Consumer & Industry Services, Bureau of Safety and Regulation, Wage and Hour Division, 7150 Harris Drive, P.O. Box 30476, Lansing, Michigan 48909-7976 http://www.michigan.gov/dleg/0,1607,7-154-27673_27706-39650--,00.html

Wayne State University's Prevailing Wage Requirements:

When compensation will be paid under prevailing wage requirements, the University shall require the following:

- The contractor shall obtain and keep posted on the work site, in a conspicuous place, a copy of all current prevailing wage and fringe benefit rates.

- The contractor shall obtain and keep an accurate record showing the name and occupation of and the actual wages and benefits paid to each laborer and mechanic employed in connection with this contract.

- The contractor shall submit a completed certified payroll document [U.S. Department of Labor Form WH 347] verifying and confirming the prevailing wage and benefits rates for all employees and subcontractors for each payroll period for work performed on this project.  The contractor shall include copies of pay stubs for all employee or contract labor payments related to Wayne State University work.  The certified payroll form can be downloaded from the Department of Labor website at http://www.dol.gov/whd/forms/wh347.pdf.  NOTE:  Invoices WILL NOT be processed until certified payrolls are received.

If the VENDOR or subcontractor fails to pay the prevailing rates of wages and fringe benefits and does not cure such failure within 10 days after notice to do so by the UNIVERSITY, the UNIVERSITY shall have the right, at its option, to do any or all of the following:

1.	Withhold all or any portion of payments due the VENDOR as may be considered necessary by the UNIVERSITY to pay laborers and mechanics the difference between the rates of wages and fringe benefits required  by this contract and the actual wages and fringe benefits paid;

2.	Terminate this contract and proceed to complete the contract by separate agreement with another vendor or otherwise, in which case the VENDOR and its sureties shall be liable to the UNIVERSITY for any excess costs incurred by the UNIVERSITY.

3.	Propose to the Assistant Vice President that the Vendor be considered for Debarment in accordance with the University’s Debarment Policy, found on our website at 
http://purchasing.wayne.edu/docs/appm28.pdf

Terms identical or substantially similar to this section of this RFP shall be included in any contract or subcontract pertaining to this project.

The current applicable prevailing wage rates as identified by the State of Michigan Department of Consumer & Industry Services, Bureau of Safety and Regulation, Wage and Hour Division are listed below for reference.  Refer to item C above if additional information is required.

<See Purchasing Website at:

http://purchasing.wayne.edu/vendors/wage-rates.php  .

AA.  	Buy  American

Wayne State University intends to purchase products in the United States of America whenever an American made* product is available that meets or exceeds the specifications requested and the price is equal to or lower than a foreign made product.  Vendors are required to bid American made products whenever available.  Vendors may bid foreign made products when:

1)  They are specified

2)   As an alternate as long as they are technically equal to the product specified.

*  (More than  50% of the product manufactured or assembled in the U.S.A.)

Schedule A

RESPONSE TO WAYNE STATE UNIVERSITY

REQUEST FOR PROPOSAL

## RFP:  C & IT Air Conditioning and Maintenance Services 2013, Project R575373

AND TO ANY AMENDMENTS, THERETO

DATED:  May 3, 2013

PROPOSAL CERTIFICATION, ACKNOWLEDGEMENTS,

and NON_COLLUSION AFFIDAVIT

VENDOR is to certify its proposal as to its compliance with the Request for Proposal specifications using the language as stated hereon.

ACKNOWLEDGEMENTS

By virtue of submittal of a Proposal, VENDOR acknowledges and agrees that:

- All of the requirements in the Scope of Work of this RFP have been read, understood and accepted.

- The University’s General Requirements and Guidelines have been read, understood and accepted.

- Compliance with the Requirements and/or Specifications, General Requirements and Guidelines, and any applicable Supplemental Terms and Conditions will be assumed acceptable to the VENDOR if not otherwise noted in the submittal in an Exhibit I, Restricted Services.

- The Supplier is presently not debarred, suspended, proposed for debarment, declared ineligible, nor voluntarily excluded from covered transactions by any Federal or State of Michigan department or agency.

- Wayne State University is a constitutionally autonomous public university within Michigan's system of public colleges and universities, and as such, is subject to the State of Michigan Freedom of Information Act 442 of 1976.  Any Responses Proposals, materials, correspondence, or documents provided to the University are subject to the State of Michigan Freedom of Information Act, and may be released to third parties in compliance with that Act, regardless of notations in the VENDOR's Proposal to the contrary.

- All of the Terms and Conditions of this RFP and Vendor’s Response Proposal become part of any ensuing agreement.

- The individual signing below has authority to make these commitments on behalf of Supplier.

- This proposal remains in effect for [120] days.

VENDOR, through the signature of its agent below, hereby offers to provide the requested products/services at the prices specified, and under the terms and conditions stated and incorporated into this RFP.

PROPOSAL CERTIFICATION

The undersigned, duly authorized to represent the persons, firms and corporations joining and participating in the submission of this Proposal states that the Proposal contained herein is complete and is in strict compliance with the requirements of the subject Request for Proposal dated May 3, 2013, except as noted in Exhibit 1, the "Restricted Services/Exceptions to RFP" section of the Proposal.  If there are no modifications, deviations or exceptions, indicate “None” in the box below:

|  | NONE – There are no exceptions to the University’s requirements or terms |
| --- | --- |

|  | YES – Exceptions exist as shown in Exhibit 1, Restricted Services. |
| --- | --- |

NON-COLLUSION AFFIDAVIT

The undersigned, duly authorized to represent the persons, firms and corporations joining and participating in the submission of the foregoing Proposal, states that to the best of his or her belief and knowledge no person, firm or corporation, nor any person duly representing the same joining and participating in the submission of the foregoing Proposal, has directly or indirectly entered into any agreement or arrangement with any other VENDORS, or with any official of the UNIVERSITY or any employee thereof, or any person, firm or corporation under contract with the UNIVERSITY whereby the VENDOR, in order to induce acceptance of the foregoing Proposal by said UNIVERSITY, has paid or is to pay to any other VENDOR or to any of the aforementioned persons anything of value whatever, and that the VENDOR has not, directly or indirectly entered into any arrangement or agreement with any other VENDOR or VENDORS which tends to or does lessen or destroy free competition in the letting of the contract sought for by the foregoing Proposal.

The VENDOR hereby certifies that neither it, its officers, partners, owners, providers, representatives, employees and parties in interest, including the affiant, have in any way colluded, conspired, connived or agreed, directly or indirectly, with any other proposer, potential proposer, firm or person, in connection with this solicitation, to submit a collusive or sham bid, to refrain from bidding, to manipulate or ascertain the price(s) of other proposers or potential proposers, or to obtain through any unlawful act an advantage over other proposers or the college.

The prices submitted herein have been arrived at in an entirely independent and lawful manner by the proposer without consultation with other proposers or potential proposers or foreknowledge of the prices to be submitted in response to this solicitation by other proposers or potential proposers on the part of the proposer, its officers, partners, owners, providers, representatives, employees or parties in interest, including the affiant.

CONFLICT OF INTEREST

The undersigned proposer and each person signing on behalf of the proposer certifies, and in the case of a sole proprietorship, partnership or corporation, each party thereto certifies as to its own organization, under penalty of perjury, that to the best of their knowledge and belief, no member of the UNIVERSITY, nor any employee, or person, whose salary is payable in whole or in part by the UNIVERSITY, has a direct or indirect financial interest in the award of this Proposal, or in the services to which this Proposal relates, or in any of the profits, real or potential, thereof, except as noted otherwise herein.

Any notice required under the Agreement shall be personally delivered or mailed by first class or certified mail, with proper postage, prepaid, to the Subject VENDOR at the following address:

Company Name:		_________________________________________________________

Address:			_________________________________________________________

_________________________________________________________

Telephone:		(________________)_______________________________________

Fax:			(________________)_______________________________________

Email address:		_________________________________________________________

Submitted by:		_________________________________________________________

Signature		_________________________________________________________

____________________________________    ___________________

(Title)                                                  (Date)

Schedule B - INSURANCE REQUIREMENTS (Rev 01-2013)

____________________________________________, at its sole expense, shall cause to be issued and maintained in full effect for the term of this agreement, insurance as set forth hereunder:

General Requirements

| Type of Insurance | Minimum Requirement |
| --- | --- |
| 1. Commercial General Liability (CGL) CGL insurance should be written on ISO form CG 00 01 (or equivalent substitute) | $1,000,000 combined single limit $2,000,000 annual aggregate |
| 2. Commercial Automobile Liability (including hired and non-owned vehicles) | $1,000,000 combined single limit per accident for bodily injury and property damage, without annual aggregate. |
| 3. Workers' Compensation (Employers' Liability) | Required by the State of Michigan and Employer’s Liability in the amount of $500,000 per accident for bodily injury or disease. |

Maximum Acceptable Deductibles

Type of Insurance			Deductible

Commercial General Liability			$5,000

Commercial Automobile Liability			 0

Workers' Compensation 			 0

Property - All Risk 			$1,000

Coverage

1.	All liability policies must be written on an occurrence form of coverage.

2.	Commercial General Liability (CGL) includes, but is not limited to: consumption or use of products, existence of equipment or machines on location, and contractual obligations to customers.

3.	The Board of Governors of Wayne State University shall be named as an additional insured, but only with respect to accidents arising out of said contract.

4. 	The additional insured provision shall contain a cross liability clause as follows: “The insurance afforded applies separately to each insured against whose claim is made or suit is brought, except with respects to the limits of the company’s liability.”

5.	The insurance company for each line of insurance coverage will be reviewed and checked per the A.M. Best’s Key Rating Guide.  A rating of not less than “A-“ is required

Certificates of Insurance

1.	Certificates of Insurance naming Wayne State University / Office of Risk Management as the certificate holder and stating the minimum required coverage must be forwarded to the Office of Risk Management to be verified and authenticated with the agent and/or insurance company.

2.	Certificates shall contain a statement from the insurer that, for this contract, the care, custody or control exclusion is waived.

3.	Certificates shall be issued on a ACORD form or one containing the equivalent wording, and require giving WSU a thirty (30) day written notice of cancellation or material change prior to the normal expiration of coverage.

4.	Revised certificates must be forwarded to the Office of Risk Management thirty (30) days prior to the expiration of any insurance coverage listed on the original certificate, as follows:

Wayne State University

Office of Risk Management

5700 Cass Avenue, Suite 4622 AAB

Detroit, MI 48202

Specific Requirements- Individual contracts may require coverage in addition to the minimum general requirement

such as, business interruption, higher limits and or blanket fidelity insurance.

Exception to the insurance requirements is to be approved, in writing, by the Office of Risk Management. Exceptions are determined by the type and nature of the contract and the individual contractor.

# Schedule C

(Cost Schedule; Compensation and Fees)

See web site:

http://www.forms.purchasing.wayne.edu/Adv_bid/Adv_bid.html

COST SCHEDULE C

RFP AIR CONDITIONING AND MAINTENANCE SERVICES 2013,

PROJECT R575373

The submittal of this bid form acknowledges agreement to the terms and conditions of the Wayne State University Service Partnership Agreement as described in Attachment D. It is further understood that this is a single contract comprised of three sections, each requiring a separate quoted price. Pricing to be to be firm and fixed for 3 years for the periods: July 1, 2013 – September 30, 2013 October 1, 2013 – September 30, 2014 October 1, 2014 – September 30, 2015 The University is to have the right to renew for two (2) optional additional twelve (12) month periods from October 1, 2015 – September 30, 2017. Vendors are to quote their maximum percentage increase for the optional additional years. Section 1 Described as C&IT Building at 5925 Woodward Section 1 is understood to be a full service contract which covers the costs of labor, parts and materials including compressor replacement for the equipment described on Appendix 4. Annual maintenance will be performed to this equipment as detailed in Attachment A. SECTION 1 FIXED PRICE QUOTE ____________ Max % Discount for Optional Years 1 _______ Max % Discount for Optional Years 2 _______ Section 2 Described as C&IT Fiber Rooms Throughout Wayne State University Campus. Section 2 is understood to be a once annual maintenance contract for the equipment described \n Appendix 5 which will be comprised of the work outlined in Attachment B. Vendors are to quote as a single price for the annual maintenance to all of the equipment detailed in Appendix 5 but for the purpose of adding equipment to the contract as needed, this price can be assumed to reflect an average price per unit. Service repairs to this equipment will be billed as time and materials per quoted rates. SECTION 2 ANNUAL MAINTENANCE PRICE QUOTE _____________ Monday - Friday 8am-4:30 pm Hourly Rate _________ Hourly Rate for service outside of normal hours _________ Max % Discount for Optional Years 1 _______ Max % Discount for Optional Years 2 _______ Described as C&IT Disaster Recovery Site Wayne State University Oakland Campus-33737 W. 12 Mile Road, Farmington Hills, MI 48331. Section 3 Section 3 is understood to be a Bi-annual maintenance contract for the equipment described on Appendix 6 which will be comprised of the work outlined in Attachment C. Vendors are to quote as a single price for the annual maintenance to all of the equipment detailed in Appendix 6. Service repairs to this equipment will be billed as time and materials per quoted rates. SECTION 3 Bi-ANNUAL MAINTENANCE PRICE QUOTE _____________ Monday - Friday 8am-4:30 pm Hourly Rate _________ Hourly Rate for service outside of normal hours _________ Max % Discount for Optional Years 1 _______ Max % Discount for Optional Years 2 _______

Schedule D - Summary Questionnaire

| 1. Can your company commence on or before July 1, 2013 and be completed by June 31, 2014? |  | YES _______ | ALTERNATIVE ______________ |
| --- | --- | --- | --- |
| 2. Does your company agree to provide a minimum of 3 references to the University upon request, with specific contact names and phone numbers? |  | _______ | ______________ |
| 3. Did you attend the mandatory Pre-Proposal meeting on May 9, 2013? |  | _______ | ______________ |
| 4. Did your company provide a certificate of insurance to meet or exceed all our minimum requirements? |  | _______ | _______________ |
| 5. Did your company provide the required Proposal Certification, Non- Collusion Affidavit and Vendor Acknowledgement, Schedule A? |  | _______ | _______________ |
| 6. Did your company complete and provide the Summary Price Schedule C, and submit it electronically to rfp@wayne.edu? |  | _______ | _______________ |
| 7. Does your company agree to enroll in our ACH payment program? |  | _______ | ______________ |
| 8. Did your company agree to guarantee to maintain a top priority for the UNIVERSITY? |  | _______ | ______________ |
| 9. Please complete the following questions: Total number of employees in your company Total years in business with this company name |  | ______ ______ |  |
| 10. Does your company agree to provide financial reports to the University upon request? |  | _______ | ______________ |
| Does your company agree to allow the UNIVERSITY to audit your books pertaining to the UNIVERSITY account? |  | _______ | ______________ |
| Are there any conflicts of interest in doing business with the University? |  | ___ Yes ___ No |  |
| 13. Did your company provide a “Restricted Services” exhibit, EXHIBIT 1? |  | ___ Yes ___ No |  |
| 14. Does your company agree to provide a list of lost accounts in excess of $25,000? |  | _______ | ______________ |
| Did your company quote services at prevailing wage rates where applicable and clearly indicate such in your proposal? |  | NA_ | ___NA______ |

- ADDENDA:	The undersigned affirms that the cost of all work covered by the following Addenda are included in the lump sum price of this proposal.

Addendum No.	     Date		      	Addendum No.	    Date

Addendum No.	     Date		     	Addendum No.	    Date

Addendum No.	     Date		     	Addendum No.	    Date

Addendum No.	     Date		     	Addendum No.	    Date

Addendum No.	     Date		     	Addendum No.	    Date

Company Name:		_________________________________________________________

Signature		_________________________________________________________

Typed Name		_________________________________________________________

____________________________________    ___________________

(Title)                                                  (Date)

APPENDIX 1

(Wayne State University Campus Map)

See web site:

http://campusmap.wayne.edu/

A detailed list of Cash & Coin operated lots can be viewed at http://purchasing.wayne.edu/cash_and_credit_card_lots.php

APPENDIX 2

REGISTRATION/INTENT FORM

## RFP:  C & IT Air Conditioning and Maintenance Services 2013, Project R575373 / RLK

Please use this form to indicate your attendance at our mandatory Pre-proposal meeting to be held on, May 9, 2013 at 9:00 - 10:00 a.m. and your intent to submit a proposal for the services listed.  Please type or print the information requested below, then fax to attention Ms. Pat Milewski at (313) 577-3747 by, May 8, 2013, 12:00 noon.

VENDOR Name:	                _____

VENDOR Address:

Contact Person:

Telephone:		  (		)

Fax:			  (		)

E-mail

YES ________  I will be attending the mandatory Pre-proposal meeting on May 9, 2013

Location:	C & IT DEPARTMENT

5925 Woodward,

(Main Lobby)

Detroit, MI  48202

Time:       	9:00 - 10:00 a.m.

NO _________  I will not participate in the Request for Proposal and will not be

present at the meeting.

I understand that this will not affect our status as a potential supplier to Wayne State University.

Thank you for interest shown in working with Wayne State University.

Robert Kuhn, Sr. Buyer,

Senior Buyer

APPENDIX 3

Prevailing Wage Rates

Not Applicable

APPENDIX 4

Equipment List at C&IT 5925 Woodward

See web site:

http://www.forms.purchasing.wayne.edu/Adv_bid/Adv_bid.html

|  |  |  |  |  |  |  |  |  |  |  |  |  | Appendix 4 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | EQUIPMENT DETAILS FOR C&IT BUILDING AT 5925 WOODWARD |  |  |  |  |  |  |  |  |  |
| SYSTEM |  | LOCATION | MANUFACTURER | A/C MODEL |  | A/C SERIAL NUMBER | CONDENSER MODEL | CONDENSER SERIAL NUMBER | MAINTENANCE COVERAGE |
| First and Mezz Floor Telephone Closet A/C unit | 330 |  | YORK |  | N2AHD20A46A |  | MBTS097447 |  | UNKNOWN |  | UNKNOWN |  | 5 DAYS -- 8 HOURS |
| Computer Room Air Conditioner | 180 |  | LIEBERT #1 |  | FH290AUA00 |  | 199054-001 |  | DCDF291A |  | 3080119 |  | 5 DAYS -- 8 HOURS |
| Computer Room Air Conditioner | 180 |  | LIEBERT #2 |  | FH290AUA00 |  | 199054-002 |  | UNKNOWN |  | UNKNOWN |  | 5 DAYS -- 8 HOURS |
| Computer Room Air Conditioner | 180 |  | LIEBERT #3 |  | FH290AUASM |  | 328037-001 |  | 5000-4 |  | UNKNOWN |  | 5 DAYS -- 8 HOURS |
| Computer Room Air Conditioner | 180 |  | LIEBERT #4 |  | FH290AUASM |  | 328037-002 |  | 5000-4 |  | UNKNOWN |  | 5 DAYS -- 8 HOURS |
| Computer Room Air Conditioner | 182 |  | LIEBERT #5 |  | FH290AUASM |  | 342865-001 |  | DCDF308LA |  | 97050011 |  | 5 DAYS -- 8 HOURS |
| Computer Room Air Conditioner | 182 |  | DATAC #5 |  | CCT-20G4 |  | 8701D086 |  | PFG26 (LARKIN) | 86361391-9 |  | 5 DAYS -- 8 HOURS |
| Computer Room Air Conditioner | 182 |  | DATAC #6 |  | CCT-20G4 |  | 8701D087 |  | PFG26 (LARKIN) | 86381391-7 |  | 5 DAYS -- 8 HOURS |
| Computer Room Air Conditioner | 182 |  | DATAC #7 |  | CCT-20G4 |  | 8701D085 |  | DFT026 (BOHN) | T02D01477 |  | 5 DAYS -- 8 HOURS |
| Print Room Air Conditioner | 182 |  | DATAC #8 |  | CCT-15G4-UD |  | 8701D094 |  | PFG21 (LARKIN) | 86037124 |  | 7 DAYS -- 24 HOURS |
| Computer Room Air Conditioner | 182 |  | EDPAC |  | CDXC-21 |  | 33975-001B |  | PPGZ1 |  | 25743 |  | 5 DAYS -- 8 HOURS |
| Sub Station Air Conditioner | 162.13 |  | CARRIER |  | 50BD-024-630 |  | N896377 |  | UNKNOWN |  | UNKNOWN |  | 7 DAYS -- 24 HOURS |
| Battery Room Air Conditioner | 162.08 |  | LIEBERT |  | MCD24ALPH3 |  | 0140N54812 |  | UNKNOWN |  | UNKNOWN |  | 7 DAYS -- 24 HOURS |
| Trailer Air Conditioner | 5957 Woodward | BARD |  | WA361-A15XX4XX (HEATER) EHWA03-A15 | 125P001559739-01 | UNKNOWN |  | UNKNOWN |  | 5 DAYS -- 8 HOURS |
| Trailer Air Conditioner | 5957 Woodward | BARD |  | WA361-A15XX4XX (HEATER) EHWA03-A15 | 125P001559736-01 | UNKNOWN |  | UNKNOWN |  | 5 DAYS -- 8 HOURS |
| Trailer Air Conditioner | 5957 Woodward | BARD |  | WA361-A15XX4XX (HEATER) EHWA03-A15 | 125P001559732-01 | UNKNOWN |  | UNKNOWN |  | 5 DAYS -- 8 HOURS |
| Work Room | 130.1 |  | EMI |  | CAH24030000B | 1-98-C2122-10 |  | SCC24DFA000AA | 1-98-8848-24 |  | 5 DAYS -- 8 HOURS |

APPENDIX 5

Equipment List at C&IT Fiber Rooms

Throughout Wayne State University Campus

Appendix 5 Fiber Room Maintenance and Repair Log Building Type of Equipment Room Number Model Number Serial Number FAB LIEBERT MINIMATE 1120 MMD14W3POOHO 0217N63082 FAB LIEBERT MINIMATE 1308 MMD20W3POOHO N/A FAB LIEBERT MINIMATE 1308 MMD20W3POOHO 0217N63077 FAB LIEBERT MINIMATE 1308 MMD20W3POOHO 0217N63064 FAB LIEBERT MINIMATE 1310 MMD20W3POOHO 0217N63085 FAB LIEBERT MINIMATE 2120 MMD14W3POOHO 0217N63111 FAB LIEBERT MINIMATE 2304 MMD14W3POOHO 0217N63096 FAB LIEBERT MINIMATE 2304 MMD14W3POOHO 0217N63098 FAB LIEBERT MINIMATE 3302 MMD14W3POOHO 0217N63087 FAB LIEBERT MINIMATE 3120 MMD14W3POOHO 0217N63074 FAB LIEBERT MINIMATE 4300 MMD14W3POOHO 0217N63105 FAB LIEBERT MINIMATE 4126 MMD14W3POOHO 0217N63083 FAB LIEBERT DRY COOLER ROOF DD0347Y32 0219C56245 FAB LIEBERT PUMP PACKAGE ROOF D1.5YNT D-2002 KRESSGE. E.M.I. 12 BSMT CAH12D30000B 1-98-F-8686-24 KRESSGE. E.M.I. SCC12DAA000AA0A N/A RACKHAM LIEBERT MINIMATE BSMT MMD20W3POOHO 0321N78208 RACKHAM LIEBERT MINIMATE 1ST FLR MMD20W3POOHO 0321N78179 RACKHAM LIEBERT DRY COOLER ROOF DD0347Y32 RACKHAM LIEBERT PUMP PACKAGE ROOF D1.5YNT BIO. SCI LIEBERT MINIMATE 5TH FLR BIO. SCI LIEBERT MINIMATE 5TH FLR MMD20W3POOHO 0204N BIO. SCI LIEBERT DRY COOLER ROOF MMD14W3POOHO 0204N59337 BIO. SCI LIEBERT PUMP PACKAGE ROOF DD0158A16 0205C54391 UGL MITSUBISHI Mr. Slim PHONE RM UGL MITSUBISHI OUTDOOR PK36FL3 41G002698 UGL MITSUBISHI Mr. Slim PHONE RM PU36EK3 4ZU00945A UGL MITSUBISHI OUTDOOR PK36FL3 41G00235B SCI.&EN LIB E.M.I. OPP. RM 50 CA424D3000098 1-98-C-1962-10 SCI.&EN LIB E.M.I. SUB BSMT SCC24DF0000AA0A 1-99-C-6399-11 BUS. ADMIN LIEBERT MINIMATE BSMT MMD18E-P0000 0217N63075 BUS. ADMIN LIEBERT DX COND. CLG BSMT PFH020A-PL3 0217N63067 BUS. ADMIN LIEBERT MINIMATE BSMT MMD18E-P0000 0217N63081 BUS. ADMIN LIEBERT DX COND. CLG BSMT PFH020A-PL3 0217N63080 BUS. ADMIN LIEBERT MINIMATE 305 MMD12EP0000 0217N63095 BUS. ADMIN LIEBERT DX COND. 305 PFH014A-PL3 0217N63099 MANOOGIAN ATS 397 OHS-012-HW-SF OOO6018 EDUCATION LIEBERT MINIMATE BSMT MMD20W3P00HO EDUCATION LIEBERT MINIMATE 355 MMD20W3P00HO EDUCATION LIEBERT DRY COOLER ROOF DD092Y6 EDUCATION LIEBERT PUMP PACKAGE ROOF OLD MAIN MITSUBISHI Mr.Slim Phone Rm PKA-A24FA 51A00214B OLD MAIN MITSUBISHI Mr.Slim Courtyard PUY-A24NHA

APPENDIX 6

Equipment List at Wayne State University

Oakland Campus

|  |  |  |  |  |  |  | Appendix 6 |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | OAKLAND CENTER D/R SITE EQUIPMENT LIST |  |  |
| Type of Equipment | Manufacturer | Room Number | Model Number | Serial Number |
| Humidifier | Nortec |  | 702 |  | NHTC-020 | 2076117 |
| Package A/C | Trane |  | Exterior |  | TFH240E400BB | 101810019D |
| Package A/C | Trane |  | Exterior |  | TFH240E400BB | 101810055D |
| Package A/C | Trane |  | Exterior |  | TFH240E400BB | 101810082D |
| Package A/C | Trane |  | Exterior |  | TFH240E400BB | 101810073D |

Attachment A

RFP C & IT Air Conditioning Service and Maintenance 2013,

Project R575373

ANNUAL MAINTENANCE REQUIREMENTS AT C&IT 5925 WOODWARD.

Blower Section

- CHECK SHEAVE ALIGNMENT

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION    ( replacement belt must be Teflon)

- REPLACE FILTER (four times annually)

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL

- CHECK SYSTEM FOR LEAKS

- CHECK REFRIGERANT PRESSURES

- CHECK OIL LEVEL AND MOISTURE INDICATORS

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidification Section

- REMOVE AND CLEAN HUMIDIFIER DRAIN PAN

- INSPECT FLOAT OPERATION

- INSPECT INFRARED LAMP OPERATION

- INSPECT ELECTRICAL WIRING AND CONNECTIONS.

- REPLACE DATAC HUMIDIFICATION CYLINDER ANNUALLY

Attachment B

RFP C & IT Air Conditioning Service and Maintenance 2013, Project R575373

MAINTENANCE REQUIREMENTS AT C&IT FIBER ROOMS THROUGHOUT WAYNE STATE UNIVERSITY CAMPUS

Blower Section

- CHECK SHEAVE ALIGNMENT WHERE APPLICABLE.

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION WHERE APPLICABLE

- REPLACE FILTER ANNUALLY

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL.

- CHECK CONDENSATE DRAINLINE FOR OBSTRUCTIONS.

- CHECK SYSTEM FOR LEAKS.

- CHECK REFRIGERANT PRESSURES.

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidification Section

- CLEAN AND INSPECT

- VERIFY PROPER OPERATION..

Attachment C

RFP C & IT Air Conditioning Service and Maintenance 2013, Project R575393

BI-ANNUAL MAINTENANCE REQUIREMENTS AT DISASTER RECOVERY SITE AT WAYNE STATE UNIVERSITY OAKLAND CAMPUS

Blower Section

- CHECK SHEAVE ALIGNMENT WHERE APPLICABLE.

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION WHERE APPLICABLE

- REPLACE FILTER

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL.

- CHECK CONDENSATE DRAINLINE FOR OBSTRUCTIONS.

- CHECK SYSTEM FOR LEAKS.

- CHECK REFRIGERANT PRESSURES.

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidifier

- CLEAN AND INSPECT

- VERIFY PROPER OPERATION.

- REPLACE HUMIDIFICATION CYLINDER ANNUALLY

WAYNE STATE UNIVERSITY

STANDARD SERVICE PROVIDER AGREEMENT

This Agreement is made by and between Wayne State University, 5700 Cass Avenue, suite 4200, Detroit, Michigan 48202, a constitutional body corporate of the State of Michigan ("University") and, Supplier Name, Supplier Address, Supplier City State and Zip (the “Contractor”).

For good and valuable consideration, the parties agree as follows:

- General Purpose.  The general purpose of this Agreement is to engage the services of the Contractor to provide Air Conditioning and Maintenance Services for the University’s C & IT Department, per the University RFP dated Quote Date and the Contractor’s response Proposal dated Bid Date.  The University has assigned Larry Bott as the Contract Administrator for contract related matters.  Only contract directives from the University’s Procurement and Strategic Sourcing Department or the Contract Administrator shall be accepted by the Contractor.  Individual work preventative maintenance and service work must be coordinated and scheduled with the C & IT Department’s Contract Administrator and Project Manager, above.  All such work shall be governed by these terms.

- This Agreement provides for Air Conditioning Services and Maintenance for the University’s C & IT Department.  all work must be performed by a qualified licensed Journeyman Refrigeration Mechanics.  A detailed listing of expectations and requirements are noted in the Scope of Agreement of the RFP and in Section 1, 2, & 3 (attached).

The Contractor shall furnish all the labor, materials, equipment, services, and supervision to perform all the work identified in the “Scope of Work” in the aforementioned RFP, and approved by the C & IT Contract Administrator and Project Manager.

- Term.  The contract period shall be for an initial time period of up to 1 year, thru September 30, 2013, with the option to renew for up to two additional one year periods of service, thru September 30, 2015.  Renewal is contingent upon both parties agreeing, in writing, to do so, based on satisfaction of the price and the Contractor’s performance.

This Agreement may be terminated by the University or by the Contractor upon thirty (30) days’ written notice to the other party, or immediately by the University pursuant to paragraph 11, below.

- General Duties of the Contractor.  The Contractor shall provide the University with Air Conditioning and Maintenance Services for the University’s C & IT Department of superior quality, at competitive pricing, as described in the Statement of Work section of the Request for Quote or Proposal, which is incorporated by reference into this Agreement.

- Commencement and Completion.  Work shall be commenced immediately after execution of this Agreement.  Time is of the essence in commencing, prosecuting and completing Work in accordance with this Agreement.

The work to be performed under this Agreement will extend through September 30, 2013, with the University option to renew for up to two additional one-year periods.  The contract would be amended in writing for years 2 and 3 should the option be exercised by the University.  Separate Purchase Orders would be issued for each year.

5.	Contract Sum.  The University shall pay the Contractor per invoicing for the performance of all work associated with the Contractor’s fee schedule, as provided in the Contractor’s proposal dated Bid Date, provided to the University in response to the __RFP C & IT Air Conditioning and Maintenance Services 2013, Project R575373__dated Quote Date.    All work must be approved by the C & IT Facilities Operations Contract Administrator/Project Manager.

- Payments.  As an express condition precedent to any obligation on the part of the University to make any payment to the Contractor, the Contractor shall submit properly and fully executed invoice, along with the required Reports as outlined in the attachments and agreed upon with the C & IT Contract Administrator/Project Manager.

University shall not be obligated to release any payment to the Contractor in the absence or incompleteness of any of the required documentation.

A duly executed and submitted invoice by the Contractor shall constitute a warranty and representation that all of the Work provided is in conformance with this Agreement and any other contract documents, is in conformance with all legal requirements, and is free from defects in materials and/or workmanship.

No accepted Invoice, nor any payment by the University, nor any partial or entire use of the premises by the University shall constitute acceptance of any Work by the Project Manager which was not performed in accordance with legal requirements, this Agreement and any other contract documents, or in a good and workmanlike manner.

In the event that the Contractor persistently fails to correct nonconforming work, University may give Contractor written notice immediately, proceed to correct the Work and retain or withhold from the Contractor's Invoice sums sufficient to reimburse University of the cost of such corrections.

Contractor warrants that title to all Work on this Project including materials and equipment shall be free and clear of any liens, claims, security interests or encumbrances and as necessary shall pass to University upon receipt of payment by the Contractor.  Contractor shall defend, indemnify and hold University harmless from any and all costs, fees and expenses, including attorney's fees, relating in any way to filings, actions, or proceedings brought against the University or University's property as a result of liens filed or threatened against the site of the Work or otherwise.  Contractor shall pay all claims, fees and expenses including any judgment, against the University or the University's property resulting from any action, lawsuit or proceeding to collect any amounts claimed to be owed.

Payments or portions of payments may be withheld by the University on account of: (1) defective work not remedied, (2) claims filed, (3) failure of the Contractor to make payments properly to subcontractors for labor, materials or equipment, (4) damage to the University or another contractor, and/or (5) persistent failure to carry out the Work in accordance with the Contract Documents.

7.	University Obligations.  University shall make any decisions or selections necessary under the Contract Documents so as not to delay the orderly progress of the Work.

University shall pay approved and accepted Invoices submitted in conformance with the requirements of this Agreement and any other contract documents within thirty (30) days of the approved submission.

8.	Contractor Obligations.  Contractor warrants and represents that all material and equipment incorporated in the Work shall be new, unless otherwise specified, and that all Work will be of good quality, free from faults and defects and in conformance with this Agreement and any other contract documents.  Any work not conforming to these requirements shall be considered defective.

Contractor shall pay all sales, use, consumer and other similar taxes applicable to the Work and shall secure and pay for the building permits and all other governmental fees, licenses, inspections necessary for the proper execution and completion of the Work on the Project.

Contractor shall give all notices and comply with all laws, ordinances, rules, regulations and lawful orders of any public authority bearing on the performance of the Work.

Contractor shall be responsible to the University for the acts and omissions of Contractor's employees, subcontractor, suppliers and their agents and employees as well as any other person performing Work under this Agreement.

Contractor shall be solely responsible for initiating and maintaining and supervising the safety precautions and programs in connection with the Work..  Contractor shall take all reasonable precautions for the safety of, and shall provide all reasonable protection to prevent damage, injury or loss to:

- all employees or other persons affected by the Work,

- all of the Work and all materials and equipment to be incorporated in the Work, and

- other property at the site.

Contractor shall comply with all laws, regulations and ordinances bearing on the safety of persons and property.  Contractor shall promptly remedy any damage or loss to any property caused in whole or in part by Contractor or anyone for whom the Contractor is responsible.

9.	Prevailing Wages.  The Contractor and each subcontractor shall pay to each class of mechanics and laborers not less than the wage and fringe benefit rates prevailing in the Detroit Metropolitan Area, as determined by the State of Michigan Department of Energy, Labor and Economic Growth.  The Contractor shall post on site, in a conspicuous place, a copy of all applicable wage and benefit rates, and shall provide the University with a copy of the applicable wage and benefit rates.

The Contractor and each subcontractor shall keep an accurate record showing the name and occupation of and the actual benefits and wages paid to each laborer and mechanic employed in connection with this contract.  The Contractor and each subcontractor shall provide certified payroll records to the University’s representatives with each pay application.  Failure to provide certified payroll documents will result in the return of said pay application unpaid.

If Contractor or a subcontractor fails to pay the prevailing rates of wages and fringe benefits and does not cure such failure within ten (10) days after notice to do so by the University, the University shall have the right, at its option, to do any or all of the following:

  - Withhold all or any portion of payments due the Contractor as may be considered necessary by the University to pay laborers and mechanics the difference between the rates of wages and fringe benefits required by this Agreement and the actual wage and fringe benefits paid.

  - Terminate part or all of this Agreement or any subagreement and proceed to complete the Agreement or subagreement by separate agreement with another contractor or otherwise, in which case the Contractor shall be liable to the University for any excess costs incurred by the University.

The Contractor shall include terms identical or substantially similar to this section in any agreement or subagreement pertaining to the Project.

10.	Order Process.  The University will issue a Blanket Purchase Order for the Contracted Period for Air Conditioning Services and Maintenance by the Contractor.   The University will issue separate purchase orders for each additional optional year of coverage.  The Contractor is to invoice against each individual Purchase Order according to individual purchase order time periods and terms.

The terms and conditions of this Agreement, along with the University RFP dated Quote Date and the Contractor’s response Proposal dated Bid Date, govern and supersede the standard terms and conditions of Purchase of individual Purchase Orders, regardless of whether said Purchase Orders specifically reference back to the Agreement. The Contractor’s shipment of goods or provision of services in response to a Purchase Order shall constitute acceptance of the Purchase Order.  Acceptance of a Purchase Order is limited to its express terms.

11.	Independent Contractor.  The parties expressly acknowledge that the Contractor is an independent contractor.  The Contractor is not an agent, partner, or employee of the University.  The Contractor shall not have the authority to enter into any contract or agreement to bind the University and shall not represent to anyone that the Contractor has such authority.  The Contractor represents and warrants to the University that in performing the Services, the Contractor will not be in breach of any agreement with a third party.  The Contractor declares that it is not a legislator, elected or appointed officer, or that it is not owned or controlled by any legislator, elected or appointed officer, compensated or uncompensated, member of a State board or commission, or other employee of the State of Michigan (including an employee, officer, or official of Wayne State University).  The Contractor agrees that it is subject to the University’s regulations, laws of the United States and of the State of Michigan, and that, in the event of violation of these, or behavior that is considered to be detrimental to the University or its students, faculty or staff; the University shall have the right to terminate this Agreement without prior notice.

12.	General Statement of Work.  The Contractor shall plan, organize, manage, supply and support Air Conditioning and Maintenance Services, per the following and per the attachments:

Section 1 SCOPE OF AGREEMENT FOR C&IT BUILDING AT 5925 WOODWARD Contractor will agree that all work will be performed by qualified licensed Journeyman Refrigeration Mechanics. Contractor will agree to maintain a record of refrigerant usage on each piece of equipment and provide a copy to Wayne State C&IT Facilities department due annually on September 30th. Contractor will maintain a record of all work performed to each piece of equipment covered under contract and provide an electronic copy to Wayne State C&IT Facilities department due annually on September 30th. Work sheets detailing work performed and hours worked will be turned in to Wayne State C&IT Facilities department at the end of each work day. Upon completion of each assignment or repair a summary work sheet will be submitted detailing the required repairs. This will include a detailed copy of the maintenance inspection checklist for the required maintenance on each piece of equipment. Contract will include parts and materials including replacement compressors. Contract will include labor during designated hours of 8:00 am to 4:30 pm Monday-Friday. Contractor will agree to provide emergency call number and service within 4 hours of call. Contractor will agree to provide service within 24 hours of call unless otherwise agreed with Wayne State C&IT Facilities department. Contractor will schedule maintenance visits to assure periodic maintenance for inspections, coil cleaning and filter changes on a quarterly basis. Contractor will agree to perform condenser and dry-cooler maintenance after May 1st and no later than June 5th of each year. This work will require the application of a nickel safe foam type coil cleaning agent followed by a clean water rinse with a pressure washer. Section 2 SCOPE OF AGREEMENT FOR C&IT FIBER ROOMS THROUGHOUT WAYNE STATE UNIVERSITY CAMPUS Contractor will agree that all work will be performed by qualified licensed Journeyman Refrigeration Mechanics. Contractor will agree to maintain a record of refrigerant usage on each piece of equipment and provide a copy to Wayne State C&IT Facilities department due annually on September 30th. Contractor will maintain a record of all work performed to each piece of equipment covered under contract and provide a copy to Wayne State C&IT Facilities department due annually on September 30th. Work sheets detailing work performed and hours worked will be turned in to Wayne State C&IT Facilities department at the end of each work day. Upon completion of each assignment or repair a summary work sheet will be submitted detailing the required repairs. This will include a detailed copy of the maintenance inspection checklist for the required maintenance on each piece of equipment. Contract will provide labor rate for services during designated hours of 8:00 am to 4:30 pm Monday-Friday. Service work will be billed time and material. Contract will provide labor rate for emergency service outside of normal hours designated above. Emergency service will be billed as time and material Contractor will agree to provide emergency service within 4 hours of call. Contractor will agree to provide service within 24 hours of call unless otherwise agreed with Wayne State C&IT Facilities department. Contract will indicate a fixed price for completion of the annual maintenance detailed on attachment C for all equipment listed on attachment D. This fixed price will be figured as an average annual maintenance cost per unit so that future installations can be added if need arises. Contractor will schedule one annual maintenance visit for each air conditioning unit to assure periodic maintenance is completed no earlier than April 1st and prior to June 5th of each year. Contractor will agree to perform condenser and dry-cooler maintenance and cleaning after April 15th and no later than June 5th of each year. Contract will identify cost mark-up on repair parts in percentage terms, verifiable on request of Wayne State University C&IT Facilities department. Wayne State University C&IT Facilities department will accept supplier invoice as proof. Section 3 SCOPE OF AGREEMENT FOR DISASTER RECOVERY SITE AT WAYNE STATE UNIVERSITY OAKLAND CAMPUS Contractor will agree that all work will be performed by qualified licensed Journeyman Refrigeration Mechanics. Contractor will agree to maintain a record of refrigerant usage and provide a copy to Wayne State C&IT Facilities department due annually on September 30th. Contractor will maintain a record of all work performed to each piece of equipment covered under contract and provide a copy to Wayne State C&IT Facilities department due annually on September 30th. Work sheets detailing work performed and hours worked will be turned in to Wayne State C&IT Facilities department upon completion of each assignment or repair. Contract will provide labor rate for services during designated hours of 8:00 am to 4:30 pm Monday-Friday. Service work will be billed time and material. Contract will provide labor rate for emergency service outside of normal hours designated above. Emergency service will be billed as time and material Contractor will agree to provide emergency service within 4 hours of call. Contractor will agree to provide service within 24 hours of call unless otherwise agreed with Wayne State C&IT Facilities department. Contract will indicate a fixed price for completion of the annual maintenance detailed on attachment E for all equipment listed on attachment F. Contractor will schedule one annual maintenance visit for each air conditioning unit to assure periodic maintenance is completed no earlier than April 1st and prior to June 5th of each year. Contractor will agree to perform condenser maintenance and cleaning after April 15th and no later than June 5th of each year. Contract will identify cost mark-up on repair parts in percentage terms, verifiable on request of Wayne State University C&IT Facilities department. Wayne State University C&IT Facilities department will accept supplier invoice as proof.

13.	Confidentiality of Information.  The Contractor agrees to keep confidential and not to disclose to third parties any information provided by the University pursuant to this Agreement unless the Contractor has received prior written consent of the University to make such disclosure.  This obligation of confidentiality does not extend to any information that:  (1) Was in the possession of the Contractor at the time of disclosure by the University, directly or indirectly; (2) Is or has become, through no fault of the Contractor, available to the general public; or (3) Is independently developed and hereafter supplied to the Contractor by a third party without restriction on disclosure.  This provision shall survive expiration and termination of this Agreement.

14.	Confidentiality and Non-Disclosure Agreement. (Deleted)

15.	Property Rights and Reports.  The Contractor agrees that any computer programs, software, documentation, copyrightable work, discoveries, inventions, improvements, or other products developed by the Contractor solely, or with others, resulting from the performance of this Agreement are the property of the University, and the Contractor agrees to assign all rights therein to the University.  The Contractor further agrees to provide the University with any assistance which the University may require to obtain patents or copyright registrations, including the execution of any documents submitted by the University.  This provision shall survive expiration and termination of this Agreement.

16.	Suspension or Termination of Contract.  The University reserves the right to suspend or terminate the contract and the performance to be rendered under this Agreement by the Contractor, for any reason upon 30 days’ written notice to the Contractor.

17.	Insurance.  The Contractor, at its sole expense, shall cause to be issued and maintained in full effect for the term of this Agreement, insurance as set forth hereunder.

General Requirements Type of Insurance Minimum Requirement 1. Commercial General Liability (CGL) CGL insurance should be written on ISO form CG 00 01 (or equivalent substitute) $1,000,000 combined single limit $2,000,000 annual aggregate 2. Commercial Automobile Liability (including hired and non-owned vehicles) $1,000,000 combined single limit per accident for bodily injury and property damage, without annual aggregate. 3. Workers' Compensation (Employers' Liability) Required by the State of Michigan and Employer’s Liability in the amount of $500,000 per accident for bodily injury or disease. Maximum Acceptable Deductibles Type of Insurance Deductible Comprehensive General Liability $5,000 Comprehensive Automobile Liability 0 Workers' Compensation 0 Property - All Risk $1,000 Coverage 1. All liability policies must be written on an occurrence form of coverage. 2. Commercial General Liability (CGL) includes, but is not limited to: personal injury, property damage, consumption or use of products, existence of equipment or machines on location, and contractual obligations to customers. 3. The Board of Governors of Wayne State University shall be named as an additional insured, but only with respect to accidents arising out of said contract, on any of Contractor’s or its subcontractors’ insurance policies. 4. The additional insured provision shall contain a cross liability clause as follows: “The insurance afforded applies separately to each insured against whose claim is made or suit is brought, except with respects to the limits of the company’s liability.” Certificates of Insurance 1. Certificates of Insurance naming Wayne State University / Office of Risk Management as the certificate holder and stating the minimum required coverage must be forwarded to the Office of Risk Management to be verified and authenticated with the agent and/or insurance company. 2. Certificates shall contain a statement from the insurer that, for this contract, the care, custody, or control exclusion is waived. 3. Certificates shall be issued on a ACORD form or one containing the equivalent wording, and require giving WSU a thirty (30) day written notice of cancellation or material change prior to the normal expiration of coverage. 4. Revised certificates must be forwarded to the Office of Risk Management thirty (30) days prior to the expiration of any insurance coverage listed on the original certificate, as follows: Wayne State University Office of Risk Management 5700 Cass Avenue, Suite 4622 AAB Detroit, MI 48202 Additional Requirements. The Contractor shall either require each of its subcontractors or suppliers to procure and maintain during the life of the subcontract the same insurance types and in the same amounts as specified in this paragraph, above, or insure the activity of its subcontractors on its own policy.

18.	Indemnification and Hold Harmless.  The Contractor agrees that any personal injury to the Contractor or third parties or any property damage incurred in the course of performance of this Agreement shall be the responsibility of the Contractor.  The Contractor agrees to indemnify, defend, and hold harmless the University, its governing board, officers, employees, agents, and students from and against any and all costs, losses, damages, liabilities, expenses, demands, and judgments, including court costs and attorneys’ fees, whether for personal injury or property damage or any other claim, which may arise out of the Contractor’s performance of this Agreement whether caused in whole or in part by the Contractor or anyone for whom the Contractor is responsible, regardless of whether or not it is caused in part by the University.

19.	Notice.  Any notice to either party hereunder must be in writing signed by the party giving it and shall be served either personally or by registered or certified mail addressed as follows:

| To the University: Wayne State University Kenneth Doherty, Assistant VP Procurement & Strategic Sourcing 5700 Cass Avenue, Suite 4200 Detroit, MI, 48202 |  | Supplier Name: |
| --- | --- | --- |

or to such other addresses as may be hereafter designated by written notice.  All such notices shall be effective only when received by the addressee.

20.	Entire Agreement; Modification.  This Agreement, along with the University RFP dated Quote Date and the Contractor’s response Proposal dated Bid Date (and its attachments, if any), and subsequent clarifications, constitute the entire agreement between the parties with respect to the subject matter hereof and may not be amended except by an agreement signed by the Contractor and an authorized representative of the University.

21.	Severability.  The terms of this Agreement are severable such that if any term or provision is declared by a court of competent jurisdiction to be illegal, void, or unenforceable, the remainder of the provisions shall continue to be valid and enforceable.

22.	Governing Law and Compliance.  This Agreement shall be governed by and construed under the laws of the State of Michigan, without regard to its choice of law rules. Any lawsuits arising from or incident to this Agreement shall be brought in the Michigan Court of Claims. Each party will be individually responsible for compliance with all laws, including anti-discrimination laws, which may be applicable to their respective activities under this Agreement.

23.	Non-Waiver.  The delay or failure of either party to exercise any of its rights under this Agreement for a breach thereof shall not be deemed to be a waiver of such rights, nor shall the same be deemed to be a waiver of any subsequent breach, either of the same provision or otherwise.

24.	Assignment.  The Contractor may not assign the rights or obligations under this Agreement without the University’s prior written consent.

25.	Authority.  The parties warrant that they have the authority to enter into this Agreement and that entering into this Agreement is not restricted or prohibited by any existing agreement to which they are parties.

26.	Non Exclusivity.  This Agreement does not create an exclusive relationship between the University and the Contractor.  The University reserves the right to use other service providers, either through the other Preferred Vendor agreements executed as a result of the RFP, or non-preferred service providers in the event it is determined to be in the best interest of the University, its employees, students, or staff.

27. Warranties.  Contractor represents and warrants the following to the University in addition to any other representations or warranties contained in this Agreement or any other contract document as a material inducement to the University to execute this Agreement, which representations and warranties shall survive the execution and termination of this Agreement and the final completion of the Work:

  - Contractor and its subcontractors are financially solvent, able to pay all debts as they mature and possessed of sufficient working capital to complete the Work and perform all obligations hereunder;

  - Contractor is able to furnish the plant, tools, equipment, materials, supplies and labor required to complete the Work and perform its obligations hereunder and has sufficient experience and competence to do so; and

Contractor is authorized to do business in the State of Michigan and is properly licensed by all necessary governmental and quasi-public authorities having jurisdiction over the Contractor, the Work and the Project.

  - By execution of this document, the Contractor accepts the terms and agrees to be bound.

IN WITNESS WHEREOF, the authorized representatives of the parties have executed this Agreement on _______________.

| Wayne State University |  | Supplier Name |
| --- | --- | --- |
| Signature: |  | Signature: |
| Name: James R. Sears |  | Name: |
| Title: Associate Vice President – Facilities, Planning & Management |  | Title: |
| Date: |  | Date: |
| Phone: 313-577-4301 |  | Phone: |
| eMail: aa0830@wayne.edu |  | Phone: |

WAYNE STATE UNIVERSITY

EXHIBIT A

Price or Rate Structure

See Air Conditioning and Maintenance Service Rate Structure

ATTACHMENTS A, B, C

Attachment A

RFP C & IT Air Conditioning Service and Maintenance 2013,

Project R575373

ANNUAL MAINTENANCE REQUIREMENTS AT C&IT 5925 WOODWARD.

Blower Section

- CHECK SHEAVE ALIGNMENT

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION    ( replacement belt must be Teflon)

- REPLACE FILTER (four times annually)

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL

- CHECK SYSTEM FOR LEAKS

- CHECK REFRIGERANT PRESSURES

- CHECK OIL LEVEL AND MOISTURE INDICATORS

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidification Section

- REMOVE AND CLEAN HUMIDIFIER DRAIN PAN

- INSPECT FLOAT OPERATION

- INSPECT INFRARED LAMP OPERATION

- INSPECT ELECTRICAL WIRING AND CONNECTIONS.

- REPLACE DATAC HUMIDIFICATION CYLINDER ANNUALLY

Attachment B

RFP C & IT Air Conditioning Service and Maintenance 2013, Project R575373

MAINTENANCE REQUIREMENTS AT C&IT FIBER ROOMS THROUGHOUT WAYNE STATE UNIVERSITY CAMPUS

Blower Section

- CHECK SHEAVE ALIGNMENT WHERE APPLICABLE.

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION WHERE APPLICABLE

- REPLACE FILTER ANNUALLY

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL.

- CHECK CONDENSATE DRAINLINE FOR OBSTRUCTIONS.

- CHECK SYSTEM FOR LEAKS.

- CHECK REFRIGERANT PRESSURES.

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidification Section

- CLEAN AND INSPECT

- VERIFY PROPER OPERATION..

Attachment C

RFP C & IT Air Conditioning Service and Maintenance 2013, Project R575393

BI-ANNUAL MAINTENANCE REQUIREMENTS AT DISASTER RECOVERY SITE AT WAYNE STATE UNIVERSITY OAKLAND CAMPUS

Blower Section

- CHECK SHEAVE ALIGNMENT WHERE APPLICABLE.

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION WHERE APPLICABLE

- REPLACE FILTER

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL.

- CHECK CONDENSATE DRAINLINE FOR OBSTRUCTIONS.

- CHECK SYSTEM FOR LEAKS.

- CHECK REFRIGERANT PRESSURES.

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidifier

- CLEAN AND INSPECT

- VERIFY PROPER OPERATION.

REPLACE HUMIDIFICATION CYLINDER ANNUALLY

Attachment A

RFP C & IT Air Conditioning Service and Maintenance 2013,

Project R575373

ANNUAL MAINTENANCE REQUIREMENTS AT C&IT 5925 WOODWARD.

Blower Section

- CHECK SHEAVE ALIGNMENT

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION    ( replacement belt must be Teflon)

- REPLACE FILTER (four times annually)

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL

- CHECK SYSTEM FOR LEAKS

- CHECK REFRIGERANT PRESSURES

- CHECK OIL LEVEL AND MOISTURE INDICATORS

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidification Section

- REMOVE AND CLEAN HUMIDIFIER DRAIN PAN

- INSPECT FLOAT OPERATION

- INSPECT INFRARED LAMP OPERATION

- INSPECT ELECTRICAL WIRING AND CONNECTIONS.

- REPLACE DATAC HUMIDIFICATION CYLINDER ANNUALLY

Attachment B

RFP C & IT Air Conditioning Service and Maintenance 2013, Project R575373

MAINTENANCE REQUIREMENTS AT C&IT FIBER ROOMS THROUGHOUT WAYNE STATE UNIVERSITY CAMPUS

Blower Section

- CHECK SHEAVE ALIGNMENT WHERE APPLICABLE.

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION WHERE APPLICABLE

- REPLACE FILTER ANNUALLY

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL.

- CHECK CONDENSATE DRAINLINE FOR OBSTRUCTIONS.

- CHECK SYSTEM FOR LEAKS.

- CHECK REFRIGERANT PRESSURES.

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidification Section

- CLEAN AND INSPECT

- VERIFY PROPER OPERATION..

Attachment C

RFP C & IT Air Conditioning Service and Maintenance 2013, Project R575393

BI-ANNUAL MAINTENANCE REQUIREMENTS AT DISASTER RECOVERY SITE AT WAYNE STATE UNIVERSITY OAKLAND CAMPUS

Blower Section

- CHECK SHEAVE ALIGNMENT WHERE APPLICABLE.

- INSPECT BEARINGS

- INSPECT WHEEL FOR DIRT BUILD-UP.

- CHECK V-BELT TENSION WHERE APPLICABLE

- REPLACE FILTER

Refrigeration Section

- INSPECT AND CLEAN EVAPORATOR COIL.

- CHECK CONDENSATE DRAINLINE FOR OBSTRUCTIONS.

- CHECK SYSTEM FOR LEAKS.

- CHECK REFRIGERANT PRESSURES.

- CHECK CONDENSATE PUMP FOR OPERATION

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION.

Condenser Section

- CLEAN CONDENSER AND DRY COOLER COILS USING A NICKLE SAFE FOAM TYPE CLEANING PRODUCT OR EQUIVALENT, RINSE USING POWER WASHER.

- INSPECT ELECTRICAL COMPONANTS, PERFORM TERMINAL INTEGRITY INSPECTION

- CHECK CONTROL OPERATION

- INSPECT FAN BLADES

- CHECK FAN MOTOR OPERATION

- LEAK CHECK FOR REFRIGERANT AND GLYCOL LEAKS AS APPROPRIATE.

- SAMPLE GLYCOL CONCENTRATION FOR LOW TEMPERATURE OPERATION.

Humidifier

- CLEAN AND INSPECT

- VERIFY PROPER OPERATION.

- REPLACE HUMIDIFICATION CYLINDER ANNUALLY